## Modbus memmap of WR433 V1.7
MODBUS MEMORY MAP of WR433-03 Version 1.7
For Simple operation, just set up the "ADDING WIRELESS SENSORS"
| (1) | (2) | (3) | (4) | (5) |  | (6) | (7) | (8) | (9) | (10) | (11) | (12)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of Register | Adr | Byte Size | Description | Range | Default | Format | Property | Comment
ADDING WIRELESS SENSORS | 40273 | 272 | 110 | 3 | 1 | 32 | 2 | num of node | 0-40 | 0 | uint16 | Read/Write | Config the number of wireless sensor to connect to this Co-ordinator WR433, max 40.
| 40274 | 273 | 111 | 3 | 2 | 34 | 4 | node id 1 |  |  | uint32 | Read/Write | Config the ID number of each wireless sensor (the last 9 digits of sensor's S/N)
| 40276 | 275 | 113 | 3 | 2 | 38 | 4 | node id 2 |  |  | uint32 | Read/Write
| 40278 | 277 | 115 | 3 | 2 | 42 | 4 | node id 3 |  |  | uint32 | Read/Write
| 40280 | 279 | 117 | 3 | 2 | 46 | 4 | node id 4 |  |  | uint32 | Read/Write
| 40282 | 281 | 119 | 3 | 2 | 50 | 4 | node id 5 |  |  | uint32 | Read/Write
| 40284 | 283 | 11B | 3 | 2 | 54 | 4 | node id 6 |  |  | uint32 | Read/Write
| 40286 | 285 | 11D | 3 | 2 | 58 | 4 | node id 7 |  |  | uint32 | Read/Write
| 40288 | 287 | 11F | 3 | 2 | 62 | 4 | node id 8 |  |  | uint32 | Read/Write
| 40290 | 289 | 121 | 3 | 2 | 66 | 4 | node id 9 |  |  | uint32 | Read/Write
| 40292 | 291 | 123 | 3 | 2 | 70 | 4 | node id 10 |  |  | uint32 | Read/Write
| 40294 | 293 | 125 | 3 | 2 | 74 | 4 | node id 11 |  |  | uint32 | Read/Write
| 40296 | 295 | 127 | 3 | 2 | 78 | 4 | node id 12 |  |  | uint32 | Read/Write
| 40298 | 297 | 129 | 3 | 2 | 82 | 4 | node id 13 |  |  | uint32 | Read/Write
| 40300 | 299 | 12B | 3 | 2 | 86 | 4 | node id 14 |  |  | uint32 | Read/Write
| 40302 | 301 | 12D | 3 | 2 | 90 | 4 | node id 15 |  |  | uint32 | Read/Write
| 40304 | 303 | 12F | 3 | 2 | 94 | 4 | node id 16 |  |  | uint32 | Read/Write
| 40306 | 305 | 131 | 3 | 2 | 98 | 4 | node id 17 |  |  | uint32 | Read/Write
| 40308 | 307 | 133 | 3 | 2 | 102 | 4 | node id 18 |  |  | uint32 | Read/Write
| 40310 | 309 | 135 | 3 | 2 | 106 | 4 | node id 19 |  |  | uint32 | Read/Write
| 40312 | 311 | 137 | 3 | 2 | 110 | 4 | node id 20 |  |  | uint32 | Read/Write
| 40314 | 313 | 139 | 3 | 2 | 114 | 4 | node id 21 |  |  | uint32 | Read/Write
| 40316 | 315 | 13B | 3 | 2 | 118 | 4 | node id 22 |  |  | uint32 | Read/Write
| 40318 | 317 | 13D | 3 | 2 | 122 | 4 | node id 23 |  |  | uint32 | Read/Write
| 40320 | 319 | 13F | 3 | 2 | 126 | 4 | node id 24 |  |  | uint32 | Read/Write
| 40322 | 321 | 141 | 3 | 2 | 130 | 4 | node id 25 |  |  | uint32 | Read/Write
| 40324 | 323 | 143 | 3 | 2 | 134 | 4 | node id 26 |  |  | uint32 | Read/Write
| 40326 | 325 | 145 | 3 | 2 | 138 | 4 | node id 27 |  |  | uint32 | Read/Write
| 40328 | 327 | 147 | 3 | 2 | 142 | 4 | node id 28 |  |  | uint32 | Read/Write
| 40330 | 329 | 149 | 3 | 2 | 146 | 4 | node id 29 |  |  | uint32 | Read/Write
| 40332 | 331 | 14B | 3 | 2 | 150 | 4 | node id 30 |  |  | uint32 | Read/Write
| 40334 | 333 | 14D | 3 | 2 | 154 | 4 | node id 31 |  |  | uint32 | Read/Write
| 40336 | 335 | 14F | 3 | 2 | 158 | 4 | node id 32 |  |  | uint32 | Read/Write
| 40338 | 337 | 151 | 3 | 2 | 162 | 4 | node id 33 |  |  | uint32 | Read/Write
| 40340 | 339 | 153 | 3 | 2 | 166 | 4 | node id 34 |  |  | uint32 | Read/Write
| 40342 | 341 | 155 | 3 | 2 | 170 | 4 | node id 35 |  |  | uint32 | Read/Write
| 40344 | 343 | 157 | 3 | 2 | 174 | 4 | node id 36 |  |  | uint32 | Read/Write
| 40346 | 345 | 159 | 3 | 2 | 178 | 4 | node id 37 |  |  | uint32 | Read/Write
| 40348 | 347 | 15B | 3 | 2 | 182 | 4 | node id 38 |  |  | uint32 | Read/Write
| 40350 | 349 | 15D | 3 | 2 | 186 | 4 | node id 39 |  |  | uint32 | Read/Write
| 40352 | 351 | 15F | 3 | 2 | 190 | 4 | node id 40 |  |  | uint32 | Read/Write
MODBUS PORT CONFIG | 40257 | 256 | 100 | 3 | 1 | 0 | 2 | modbus address | 1-247 | 1 | uint16 | Read/Write
| 40258 | 257 | 101 | 3 | 1 | 2 | 2 | modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
| 40259 | 258 | 102 | 3 | 1 | 4 | 2 | modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
STATUS DATA OF 40 WIRELESS SENSORS | 40009 | 8 | 8 | 3 | 20 | 16 | 40 | rssi node 1..40 |  |  | int8 | Read | Raw RSSI value (right number must subtract 256, Unit is db)
OPERATION DATA OF 40 WIRELESS SENSORS | 30001 | 0 | 0 | 4 | 32 |  | 64 | Data area of Node 1 |  |  |  | Read | Details in sheet of sensor
| 30033 | 32 | 20 | 4 | 32 |  | 64 | Data area of Node 2 |  |  |  | Read
| 30065 | 64 | 40 | 4 | 32 |  | 64 | Data area of Node 3 |  |  |  | Read
| 30097 | 96 | 60 | 4 | 32 |  | 64 | Data area of Node 4 |  |  |  | Read
| 30129 | 128 | 80 | 4 | 32 |  | 64 | Data area of Node 5 |  |  |  | Read
| 30161 | 160 | A0 | 4 | 32 |  | 64 | Data area of Node 6 |  |  |  | Read
| 30193 | 192 | C0 | 4 | 32 |  | 64 | Data area of Node 7 |  |  |  | Read
| 30225 | 224 | E0 | 4 | 32 |  | 64 | Data area of Node 8 |  |  |  | Read
| 30257 | 256 | 100 | 4 | 32 |  | 64 | Data area of Node 9 |  |  |  | Read
| 30289 | 288 | 120 | 4 | 32 |  | 64 | Data area of Node 10 |  |  |  | Read
| 30321 | 320 | 140 | 4 | 32 |  | 64 | Data area of Node 11 |  |  |  | Read
| 30353 | 352 | 160 | 4 | 32 |  | 64 | Data area of Node 12 |  |  |  | Read
| 30385 | 384 | 180 | 4 | 32 |  | 64 | Data area of Node 13 |  |  |  | Read
| 30417 | 416 | 1A0 | 4 | 32 |  | 64 | Data area of Node 14 |  |  |  | Read
| 30449 | 448 | 1C0 | 4 | 32 |  | 64 | Data area of Node 15 |  |  |  | Read
| 30481 | 480 | 1E0 | 4 | 32 |  | 64 | Data area of Node 16 |  |  |  | Read
| 30513 | 512 | 200 | 4 | 32 |  | 64 | Data area of Node 17 |  |  |  | Read
| 30545 | 544 | 220 | 4 | 32 |  | 64 | Data area of Node 18 |  |  |  | Read
| 30577 | 576 | 240 | 4 | 32 |  | 64 | Data area of Node 19 |  |  |  | Read
| 30609 | 608 | 260 | 4 | 32 |  | 64 | Data area of Node 20 |  |  |  | Read
| 30641 | 640 | 280 | 4 | 32 |  | 64 | Data area of Node 21 |  |  |  | Read
| 30673 | 672 | 2A0 | 4 | 32 |  | 64 | Data area of Node 22 |  |  |  | Read
| 30705 | 704 | 2C0 | 4 | 32 |  | 64 | Data area of Node 23 |  |  |  | Read
| 30737 | 736 | 2E0 | 4 | 32 |  | 64 | Data area of Node 24 |  |  |  | Read
| 30769 | 768 | 300 | 4 | 32 |  | 64 | Data area of Node 25 |  |  |  | Read
| 30801 | 800 | 320 | 4 | 32 |  | 64 | Data area of Node 26 |  |  |  | Read
| 30833 | 832 | 340 | 4 | 32 |  | 64 | Data area of Node 27 |  |  |  | Read
| 30865 | 864 | 360 | 4 | 32 |  | 64 | Data area of Node 28 |  |  |  | Read
| 30897 | 896 | 380 | 4 | 32 |  | 64 | Data area of Node 29 |  |  |  | Read
| 30929 | 928 | 3A0 | 4 | 32 |  | 64 | Data area of Node 30 |  |  |  | Read
| 30961 | 960 | 3C0 | 4 | 32 |  | 64 | Data area of Node 31 |  |  |  | Read
| 30993 | 992 | 3E0 | 4 | 32 |  | 64 | Data area of Node 32 |  |  |  | Read
| 31025 | 1024 | 400 | 4 | 32 |  | 64 | Data area of Node 33 |  |  |  | Read
| 31057 | 1056 | 420 | 4 | 32 |  | 64 | Data area of Node 34 |  |  |  | Read
| 31089 | 1088 | 440 | 4 | 32 |  | 64 | Data area of Node 35 |  |  |  | Read
| 31121 | 1120 | 460 | 4 | 32 |  | 64 | Data area of Node 36 |  |  |  | Read
| 31153 | 1152 | 480 | 4 | 32 |  | 64 | Data area of Node 37 |  |  |  | Read
| 31185 | 1184 | 4A0 | 4 | 32 |  | 64 | Data area of Node 38 |  |  |  | Read
| 31217 | 1216 | 4C0 | 4 | 32 |  | 64 | Data area of Node 39 |  |  |  | Read
| 31249 | 1248 | 4E0 | 4 | 32 |  | 64 | Data area of Node 40 |  |  |  | Read
OPERATION DATA OF 40 WIRELESS SENSORS FOR ICONNECTOR (*) | 81217 | 41216 | A100 | 3 | 256 |  | 512 | Data area of Node 1 |  |  |  | Read | Details in sheet of sensor
| 81473 | 41472 | A200 | 3 | 256 |  | 512 | Data area of Node 2 |  |  |  | Read
| 81729 | 41728 | A300 | 3 | 256 |  | 512 | Data area of Node 3 |  |  |  | Read
| 81985 | 41984 | A400 | 3 | 256 |  | 512 | Data area of Node 4 |  |  |  | Read
| 82241 | 42240 | A500 | 3 | 256 |  | 512 | Data area of Node 5 |  |  |  | Read
| 82497 | 42496 | A600 | 3 | 256 |  | 512 | Data area of Node 6 |  |  |  | Read
| 82753 | 42752 | A700 | 3 | 256 |  | 512 | Data area of Node 7 |  |  |  | Read
| 83009 | 43008 | A800 | 3 | 256 |  | 512 | Data area of Node 8 |  |  |  | Read
| 83265 | 43264 | A900 | 3 | 256 |  | 512 | Data area of Node 9 |  |  |  | Read
| 83521 | 43520 | AA00 | 3 | 256 |  | 512 | Data area of Node 10 |  |  |  | Read
| 85313 | 45312 | B100 | 3 | 256 |  | 512 | Data area of Node 11 |  |  |  | Read
| 85569 | 45568 | B200 | 3 | 256 |  | 512 | Data area of Node 12 |  |  |  | Read
| 85825 | 45824 | B300 | 3 | 256 |  | 512 | Data area of Node 13 |  |  |  | Read
| 86081 | 46080 | B400 | 3 | 256 |  | 512 | Data area of Node 14 |  |  |  | Read
| 86337 | 46336 | B500 | 3 | 256 |  | 512 | Data area of Node 15 |  |  |  | Read
| 86593 | 46592 | B600 | 3 | 256 |  | 512 | Data area of Node 16 |  |  |  | Read
| 86849 | 46848 | B700 | 3 | 256 |  | 512 | Data area of Node 17 |  |  |  | Read
| 87105 | 47104 | B800 | 3 | 256 |  | 512 | Data area of Node 18 |  |  |  | Read
| 87361 | 47360 | B900 | 3 | 256 |  | 512 | Data area of Node 19 |  |  |  | Read
| 87617 | 47616 | BA00 | 3 | 256 |  | 512 | Data area of Node 20 |  |  |  | Read
| 89409 | 49408 | C100 | 3 | 256 |  | 512 | Data area of Node 21 |  |  |  | Read
| 89665 | 49664 | C200 | 3 | 256 |  | 512 | Data area of Node 22 |  |  |  | Read
| 89921 | 49920 | C300 | 3 | 256 |  | 512 | Data area of Node 23 |  |  |  | Read
| 90177 | 50176 | C400 | 3 | 256 |  | 512 | Data area of Node 24 |  |  |  | Read
| 90433 | 50432 | C500 | 3 | 256 |  | 512 | Data area of Node 25 |  |  |  | Read
| 90689 | 50688 | C600 | 3 | 256 |  | 512 | Data area of Node 26 |  |  |  | Read
| 90945 | 50944 | C700 | 3 | 256 |  | 512 | Data area of Node 27 |  |  |  | Read
| 91201 | 51200 | C800 | 3 | 256 |  | 512 | Data area of Node 28 |  |  |  | Read
| 91457 | 51456 | C900 | 3 | 256 |  | 512 | Data area of Node 29 |  |  |  | Read
| 91713 | 51712 | CA00 | 3 | 256 |  | 512 | Data area of Node 30 |  |  |  | Read
| 93505 | 53504 | D100 | 3 | 256 |  | 512 | Data area of Node 31 |  |  |  | Read
| 93761 | 53760 | D200 | 3 | 256 |  | 512 | Data area of Node 32 |  |  |  | Read
| 94017 | 54016 | D300 | 3 | 256 |  | 512 | Data area of Node 33 |  |  |  | Read
| 94273 | 54272 | D400 | 3 | 256 |  | 512 | Data area of Node 34 |  |  |  | Read
| 94529 | 54528 | D500 | 3 | 256 |  | 512 | Data area of Node 35 |  |  |  | Read
| 94785 | 54784 | D600 | 3 | 256 |  | 512 | Data area of Node 36 |  |  |  | Read
| 95041 | 55040 | D700 | 3 | 256 |  | 512 | Data area of Node 37 |  |  |  | Read
| 95297 | 55296 | D800 | 3 | 256 |  | 512 | Data area of Node 38 |  |  |  | Read
| 95553 | 55552 | D900 | 3 | 256 |  | 512 | Data area of Node 39 |  |  |  | Read
| 95809 | 55808 | DA00 | 3 | 256 |  | 512 | Data area of Node 40 |  |  |  | Read
STATUS DATA OF 40 WIRELESS SENSORS | 40029 | 28 | 1C | 3 | 1 | 56 | 2 | data status node 1 & data status node 2 | 0-9, 99 |  | byte | Read | Details in sheet of sensor
| 40030 | 29 | 1D | 3 | 1 | 58 | 2 | data status node 3 & data status node 4 | 0-9, 99 |  | byte | Read
| 40031 | 30 | 1E | 3 | 1 | 60 | 2 | data status node 5 & data status node 6 | 0-9, 99 |  | byte | Read
| 40032 | 31 | 1F | 3 | 1 | 62 | 2 | data status node 7 & data status node 8 | 0-9, 99 |  | byte | Read
| 40033 | 32 | 20 | 3 | 1 | 64 | 2 | data status node 9 & data status node 10 | 0-9, 99 |  | byte | Read
| 40034 | 33 | 21 | 3 | 1 | 66 | 2 | data status node 11 & data status node 12 | 0-9, 99 |  | byte | Read
| 40035 | 34 | 22 | 3 | 1 | 68 | 2 | data status node 13 & data status node 14 | 0-9, 99 |  | byte | Read
| 40036 | 35 | 23 | 3 | 1 | 70 | 2 | data status node 15 & data status node 16 | 0-9, 99 |  | byte | Read
| 40037 | 36 | 24 | 3 | 1 | 72 | 2 | data status node 17 & data status node 18 | 0-9, 99 |  | byte | Read
| 40038 | 37 | 25 | 3 | 1 | 74 | 2 | data status node 19 & data status node 20 | 0-9, 99 |  | byte | Read
| 40039 | 38 | 26 | 3 | 1 | 76 | 2 | data status node 21 & data status node 22 | 0-9, 99 |  | byte | Read
| 40040 | 39 | 27 | 3 | 1 | 78 | 2 | data status node 23 & data status node 24 | 0-9, 99 |  | byte | Read
| 40041 | 40 | 28 | 3 | 1 | 80 | 2 | data status node 25 & data status node 26 | 0-9, 99 |  | byte | Read
| 40042 | 41 | 29 | 3 | 1 | 82 | 2 | data status node 27 & data status node 28 | 0-9, 99 |  | byte | Read
| 40043 | 42 | 2A | 3 | 1 | 84 | 2 | data status node 29 & data status node 30 | 0-9, 99 |  | byte | Read
| 40044 | 43 | 2B | 3 | 1 | 86 | 2 | data status node 31 & data status node 32 | 0-9, 99 |  | byte | Read
| 40045 | 44 | 2C | 3 | 1 | 88 | 2 | data status node 33 & data status node 34 | 0-9, 99 |  | byte | Read
| 40046 | 45 | 2D | 3 | 1 | 90 | 2 | data status node 35 & data status node 36 | 0-9, 99 |  | byte | Read
| 40047 | 46 | 2E | 3 | 1 | 92 | 2 | data status node 37 & data status node 38 | 0-9, 99 |  | byte | Read
| 40048 | 47 | 2F | 3 | 1 | 94 | 2 | data status node 39 & data status node 40 | 0-9, 99 |  | byte | Read
| 40049 | 48 | 30 | 3 | 20 | 96 | 40 | rf timeout count node 1..40 | 0-255 |  | byte | Read | Counting the number of times that no data from wireless sensor arrived over "timeout_count_threshold" seconds , for ADVANCED diagnostic the RF connection between wireless sensor and co-ordinator
| 40069 | 68 | 44 | 3 | 1 | 136 | 2 | RF signal strength of node 1 & RF signal strength of node 2 | 0-4 |  | byte | Read | Details in sheet of sensor
| 40070 | 69 | 45 | 3 | 1 | 138 | 2 | RF signal strength of node 3 & RF signal strength of node 4 | 0-4 |  | byte | Read
| 40071 | 70 | 46 | 3 | 1 | 140 | 2 | RF signal strength of node 5 & RF signal strength of node 6 | 0-4 |  | byte | Read
| 40072 | 71 | 47 | 3 | 1 | 142 | 2 | RF signal strength of node 7 & RF signal strength of node 8 | 0-4 |  | byte | Read
| 40073 | 72 | 48 | 3 | 1 | 144 | 2 | RF signal strength of node 9 & RF signal strength of node 10 | 0-4 |  | byte | Read
| 40074 | 73 | 49 | 3 | 1 | 146 | 2 | RF signal strength of node 11 & RF signal strength of node 12 | 0-4 |  | byte | Read
| 40075 | 74 | 4A | 3 | 1 | 148 | 2 | RF signal strength of node 13 & RF signal strength of node 14 | 0-4 |  | byte | Read
| 40076 | 75 | 4B | 3 | 1 | 150 | 2 | RF signal strength of node 15 & RF signal strength of node 16 | 0-4 |  | byte | Read
| 40077 | 76 | 4C | 3 | 1 | 152 | 2 | RF signal strength of node 17 & RF signal strength of node 18 | 0-4 |  | byte | Read
| 40078 | 77 | 4D | 3 | 1 | 154 | 2 | RF signal strength of node 19 & RF signal strength of node 20 | 0-4 |  | byte | Read
| 40079 | 78 | 4E | 3 | 1 | 156 | 2 | RF signal strength of node 21 & RF signal strength of node 22 | 0-4 |  | byte | Read
| 40080 | 79 | 4F | 3 | 1 | 158 | 2 | RF signal strength of node 23 & RF signal strength of node 24 | 0-4 |  | byte | Read
| 40081 | 80 | 50 | 3 | 1 | 160 | 2 | RF signal strength of node 25 & RF signal strength of node 26 | 0-4 |  | byte | Read
| 40082 | 81 | 51 | 3 | 1 | 162 | 2 | RF signal strength of node 27 & RF signal strength of node 28 | 0-4 |  | byte | Read
| 40083 | 82 | 52 | 3 | 1 | 164 | 2 | RF signal strength of node 29 & RF signal strength of node 30 | 0-4 |  | byte | Read
| 40084 | 83 | 53 | 3 | 1 | 166 | 2 | RF signal strength of node 31 & RF signal strength of node 32 | 0-4 |  | byte | Read
| 40085 | 84 | 54 | 3 | 1 | 168 | 2 | RF signal strength of node 33 & RF signal strength of node 34 | 0-4 |  | byte | Read
| 40086 | 85 | 55 | 3 | 1 | 170 | 2 | RF signal strength of node 35 & RF signal strength of node 36 | 0-4 |  | byte | Read
| 40087 | 86 | 56 | 3 | 1 | 172 | 2 | RF signal strength of node 37 & RF signal strength of node 38 | 0-4 |  | byte | Read
| 40088 | 87 | 57 | 3 | 1 | 174 | 2 | RF signal strength of node 39 & RF signal strength of node 40 | 0-4 |  | byte | Read
| 40089 | 88 | 58 | 3 | 60 | 176 | 120 | spare |  |  | byte | Read
| 40149 | 148 | 94 | 3 | 20 | 296 | 40 | rx seq node 1..40 | 0-255 |  | byte | Read | Sequence number of data package, value from wireless sensor, for ADVANCED diagnostic of RF connecttion, to know lost of data package from sensor to Co-ordinator
| 40169 | 168 | A8 | 3 | 20 | 336 | 40 | rx duplication count node 1..40 | 0-255 |  | byte | Read | Counting the number of Dupplicated data package from sensor, to define that sensor have not received the ACK package from Co-ordinator
| 40189 | 188 | BC | 3 | 1 | 376 | 2 | sync status node 1 & sync status node 2 | 0-2, 99 |  | byte | Read | Details in sheet of sensor
| 40190 | 189 | BD | 3 | 1 | 378 | 2 | sync status node 3 & sync status node 4 | 0-2, 99 |  | byte | Read
| 40191 | 190 | BE | 3 | 1 | 380 | 2 | sync status node 5 & sync status node 6 | 0-2, 99 |  | byte | Read
| 40192 | 191 | BF | 3 | 1 | 382 | 2 | sync status node 7 & sync status node 8 | 0-2, 99 |  | byte | Read
| 40193 | 192 | C0 | 3 | 1 | 384 | 2 | sync status node 9 & sync status node 10 | 0-2, 99 |  | byte | Read
| 40194 | 193 | C1 | 3 | 1 | 386 | 2 | sync status node 11 & sync status node 12 | 0-2, 99 |  | byte | Read
| 40195 | 194 | C2 | 3 | 1 | 388 | 2 | sync status node 13 & sync status node 14 | 0-2, 99 |  | byte | Read
| 40196 | 195 | C3 | 3 | 1 | 390 | 2 | sync status node 15 & sync status node 16 | 0-2, 99 |  | byte | Read
| 40197 | 196 | C4 | 3 | 1 | 392 | 2 | sync status node 17 & sync status node 18 | 0-2, 99 |  | byte | Read
| 40198 | 197 | C5 | 3 | 1 | 394 | 2 | sync status node 19 & sync status node 20 | 0-2, 99 |  | byte | Read
| 40199 | 198 | C6 | 3 | 1 | 396 | 2 | sync status node 21 & sync status node 22 | 0-2, 99 |  | byte | Read
| 40200 | 199 | C7 | 3 | 1 | 398 | 2 | sync status node 23 & sync status node 24 | 0-2, 99 |  | byte | Read
| 40201 | 200 | C8 | 3 | 1 | 400 | 2 | sync status node 25 & sync status node 26 | 0-2, 99 |  | byte | Read
| 40202 | 201 | C9 | 3 | 1 | 402 | 2 | sync status node 27 & sync status node 28 | 0-2, 99 |  | byte | Read
| 40203 | 202 | CA | 3 | 1 | 404 | 2 | sync status node 29 & sync status node 30 | 0-2, 99 |  | byte | Read
| 40204 | 203 | CB | 3 | 1 | 406 | 2 | sync status node 31 & sync status node 32 | 0-2, 99 |  | byte | Read
| 40205 | 204 | CC | 3 | 1 | 408 | 2 | sync status node 33 & sync status node 34 | 0-2, 99 |  | byte | Read
| 40206 | 205 | CD | 3 | 1 | 410 | 2 | sync status node 35 & sync status node 36 | 0-2, 99 |  | byte | Read
| 40207 | 206 | CE | 3 | 1 | 412 | 2 | sync status node 37 & sync status node 38 | 0-2, 99 |  | byte | Read
| 40208 | 207 | CF | 3 | 1 | 414 | 2 | sync status node 39 & sync status node 40 | 0-2, 99 |  | byte | Read
CONTROL DATA OF 40 WIRELESS SENSORS | 42001 | 2000 | 7D0 | 16 | 8 |  | 16 | Control area of node 1 |  |  |  | Read/Write | Control area for each wireless sensor, see details in sheet of sensor
| 42009 | 2008 | 7D8 | 16 | 8 |  | 16 | Control area of node 2 |  |  |  | Read/Write
| 42017 | 2016 | 7E0 | 16 | 8 |  | 16 | Control area of node 3 |  |  |  | Read/Write
| 42025 | 2024 | 7E8 | 16 | 8 |  | 16 | Control area of node 4 |  |  |  | Read/Write
| 42033 | 2032 | 7F0 | 16 | 8 |  | 16 | Control area of node 5 |  |  |  | Read/Write
| 42041 | 2040 | 7F8 | 16 | 8 |  | 16 | Control area of node 6 |  |  |  | Read/Write
| 42049 | 2048 | 800 | 16 | 8 |  | 16 | Control area of node 7 |  |  |  | Read/Write
| 42057 | 2056 | 808 | 16 | 8 |  | 16 | Control area of node 8 |  |  |  | Read/Write
| 42065 | 2064 | 810 | 16 | 8 |  | 16 | Control area of node 9 |  |  |  | Read/Write
| 42073 | 2072 | 818 | 16 | 8 |  | 16 | Control area of node 10 |  |  |  | Read/Write
| 42081 | 2080 | 820 | 16 | 8 |  | 16 | Control area of node 11 |  |  |  | Read/Write
| 42089 | 2088 | 828 | 16 | 8 |  | 16 | Control area of node 12 |  |  |  | Read/Write
| 42097 | 2096 | 830 | 16 | 8 |  | 16 | Control area of node 13 |  |  |  | Read/Write
| 42105 | 2104 | 838 | 16 | 8 |  | 16 | Control area of node 14 |  |  |  | Read/Write
| 42113 | 2112 | 840 | 16 | 8 |  | 16 | Control area of node 15 |  |  |  | Read/Write
| 42121 | 2120 | 848 | 16 | 8 |  | 16 | Control area of node 16 |  |  |  | Read/Write
| 42129 | 2128 | 850 | 16 | 8 |  | 16 | Control area of node 17 |  |  |  | Read/Write
| 42137 | 2136 | 858 | 16 | 8 |  | 16 | Control area of node 18 |  |  |  | Read/Write
| 42145 | 2144 | 860 | 16 | 8 |  | 16 | Control area of node 19 |  |  |  | Read/Write
| 42153 | 2152 | 868 | 16 | 8 |  | 16 | Control area of node 20 |  |  |  | Read/Write
| 42161 | 2160 | 870 | 16 | 8 |  | 16 | Control area of node 21 |  |  |  | Read/Write
| 42169 | 2168 | 878 | 16 | 8 |  | 16 | Control area of node 22 |  |  |  | Read/Write
| 42177 | 2176 | 880 | 16 | 8 |  | 16 | Control area of node 23 |  |  |  | Read/Write
| 42185 | 2184 | 888 | 16 | 8 |  | 16 | Control area of node 24 |  |  |  | Read/Write
| 42193 | 2192 | 890 | 16 | 8 |  | 16 | Control area of node 25 |  |  |  | Read/Write
| 42201 | 2200 | 898 | 16 | 8 |  | 16 | Control area of node 26 |  |  |  | Read/Write
| 42209 | 2208 | 8A0 | 16 | 8 |  | 16 | Control area of node 27 |  |  |  | Read/Write
| 42217 | 2216 | 8A8 | 16 | 8 |  | 16 | Control area of node 28 |  |  |  | Read/Write
| 42225 | 2224 | 8B0 | 16 | 8 |  | 16 | Control area of node 29 |  |  |  | Read/Write
| 42233 | 2232 | 8B8 | 16 | 8 |  | 16 | Control area of node 30 |  |  |  | Read/Write
| 42241 | 2240 | 8C0 | 16 | 8 |  | 16 | Control area of node 31 |  |  |  | Read/Write
| 42249 | 2248 | 8C8 | 16 | 8 |  | 16 | Control area of node 32 |  |  |  | Read/Write
| 42257 | 2256 | 8D0 | 16 | 8 |  | 16 | Control area of node 33 |  |  |  | Read/Write
| 42265 | 2264 | 8D8 | 16 | 8 |  | 16 | Control area of node 34 |  |  |  | Read/Write
| 42273 | 2272 | 8E0 | 16 | 8 |  | 16 | Control area of node 35 |  |  |  | Read/Write
| 42281 | 2280 | 8E8 | 16 | 8 |  | 16 | Control area of node 36 |  |  |  | Read/Write
| 42289 | 2288 | 8F0 | 16 | 8 |  | 16 | Control area of node 37 |  |  |  | Read/Write
| 42297 | 2296 | 8F8 | 16 | 8 |  | 16 | Control area of node 38 |  |  |  | Read/Write
| 42305 | 2304 | 900 | 16 | 8 |  | 16 | Control area of node 39 |  |  |  | Read/Write
| 42313 | 2312 | 908 | 16 | 8 |  | 16 | Control area of node 40 |  |  |  | Read/Write
SYSTEM CONFIG | 40260 | 259 | 103 | 16 | 9 | 6 | 18 | serial number |  |  | string | Read/Write(PW)
| 40269 | 268 | 10C | 16 | 2 | 24 | 4 | password for setting |  |  | uint32 | Read/Write | Password = 190577, for writing co-ordinator S/N and ID
| 40271 | 270 | 10E | 16 | 2 | 28 | 4 | co-ordinator id |  |  | uint32 | Read/Write(PW)
ADVANCED CONFIG | 40400 | 399 | 18F | 16 | 1 | 286 | 2 | sync all node | 0-1 |  | uint16 | Read/Write | 1: restart sync
| 40401 | 400 | 190 | 16 | 30 | 288 | 60 | Configuration of node 1 |  |  |  | Read/Write | Configuration data area for each wireless sensor, see details in sheet of sensor
| 40431 | 430 | 1AE | 16 | 30 | 348 | 60 | Configuration of node 2 |  |  |  | Read/Write
| 40461 | 460 | 1CC | 16 | 30 | 408 | 60 | Configuration of node 3 |  |  |  | Read/Write
| 40491 | 490 | 1EA | 16 | 30 | 348 | 60 | Configuration of node 4 |  |  |  | Read/Write
| 40521 | 520 | 208 | 16 | 30 | 408 | 60 | Configuration of node 5 |  |  |  | Read/Write
| 40551 | 550 | 226 | 16 | 30 | 348 | 60 | Configuration of node 6 |  |  |  | Read/Write
| 40581 | 580 | 244 | 16 | 30 | 408 | 60 | Configuration of node 7 |  |  |  | Read/Write
| 40611 | 610 | 262 | 16 | 30 | 348 | 60 | Configuration of node 8 |  |  |  | Read/Write
| 40641 | 640 | 280 | 16 | 30 | 408 | 60 | Configuration of node 9 |  |  |  | Read/Write
| 40671 | 670 | 29E | 16 | 30 | 348 | 60 | Configuration of node 10 |  |  |  | Read/Write
| 40701 | 700 | 2BC | 16 | 30 | 408 | 60 | Configuration of node 11 |  |  |  | Read/Write
| 40731 | 730 | 2DA | 16 | 30 | 468 | 60 | Configuration of node 12 |  |  |  | Read/Write
| 40761 | 760 | 2F8 | 16 | 30 | 528 | 60 | Configuration of node 13 |  |  |  | Read/Write
| 40791 | 790 | 316 | 16 | 30 | 588 | 60 | Configuration of node 14 |  |  |  | Read/Write
| 40821 | 820 | 334 | 16 | 30 | 648 | 60 | Configuration of node 15 |  |  |  | Read/Write
| 40851 | 850 | 352 | 16 | 30 | 708 | 60 | Configuration of node 16 |  |  |  | Read/Write
| 40881 | 880 | 370 | 16 | 30 | 768 | 60 | Configuration of node 17 |  |  |  | Read/Write
| 40911 | 910 | 38E | 16 | 30 | 828 | 60 | Configuration of node 18 |  |  |  | Read/Write
| 40941 | 940 | 3AC | 16 | 30 | 888 | 60 | Configuration of node 19 |  |  |  | Read/Write
| 40971 | 970 | 3CA | 16 | 30 | 948 | 60 | Configuration of node 20 |  |  |  | Read/Write
| 41001 | 1000 | 3E8 | 16 | 30 | 1008 | 60 | Configuration of node 21 |  |  |  | Read/Write
| 41031 | 1030 | 406 | 16 | 30 | 1068 | 60 | Configuration of node 22 |  |  |  | Read/Write
| 41061 | 1060 | 424 | 16 | 30 | 1128 | 60 | Configuration of node 23 |  |  |  | Read/Write
| 41091 | 1090 | 442 | 16 | 30 | 1188 | 60 | Configuration of node 24 |  |  |  | Read/Write
| 41121 | 1120 | 460 | 16 | 30 | 1248 | 60 | Configuration of node 25 |  |  |  | Read/Write
| 41151 | 1150 | 47E | 16 | 30 | 1308 | 60 | Configuration of node 26 |  |  |  | Read/Write
| 41181 | 1180 | 49C | 16 | 30 | 1368 | 60 | Configuration of node 27 |  |  |  | Read/Write
| 41211 | 1210 | 4BA | 16 | 30 | 348 | 60 | Configuration of node 28 |  |  |  | Read/Write
| 41241 | 1240 | 4D8 | 16 | 30 | 408 | 60 | Configuration of node 29 |  |  |  | Read/Write
| 41271 | 1270 | 4F6 | 16 | 30 | 348 | 60 | Configuration of node 30 |  |  |  | Read/Write
| 41301 | 1300 | 514 | 16 | 30 | 408 | 60 | Configuration of node 31 |  |  |  | Read/Write
| 41331 | 1330 | 532 | 16 | 30 | 348 | 60 | Configuration of node 32 |  |  |  | Read/Write
| 41361 | 1360 | 550 | 16 | 30 | 408 | 60 | Configuration of node 33 |  |  |  | Read/Write
| 41391 | 1390 | 56E | 16 | 30 | 348 | 60 | Configuration of node 34 |  |  |  | Read/Write
| 41421 | 1420 | 58C | 16 | 30 | 408 | 60 | Configuration of node 35 |  |  |  | Read/Write
| 41451 | 1450 | 5AA | 16 | 30 | 348 | 60 | Configuration of node 36 |  |  |  | Read/Write
| 41481 | 1480 | 5C8 | 16 | 30 | 408 | 60 | Configuration of node 37 |  |  |  | Read/Write
| 41511 | 1510 | 5E6 | 16 | 30 | 348 | 60 | Configuration of node 38 |  |  |  | Read/Write
| 41541 | 1540 | 604 | 16 | 30 | 408 | 60 | Configuration of node 39 |  |  |  | Read/Write
| 41571 | 1570 | 622 | 16 | 30 | 348 | 60 | Configuration of node 40 |  |  |  | Read/Write
SETTING TIMEOUT VALUE OF DATA STATUS | 40354 | 353 | 161 | 16 | 1 | 194 | 2 | cmp time 1 |  | 15 | uint16 | Read/Write | Time interval for Data status = 0
| 40355 | 354 | 162 | 16 | 1 | 196 | 2 | cmp time 2 |  | 30 | uint16 | Read/Write | Time interval for Data status = 1
| 40356 | 355 | 163 | 16 | 1 | 198 | 2 | cmp time 3 |  | 45 | uint16 | Read/Write | Time interval for Data status = 2
| 40357 | 356 | 164 | 16 | 1 | 200 | 2 | cmp time 4 |  | 60 | uint16 | Read/Write | Time interval for Data status = 3
| 40358 | 357 | 165 | 16 | 1 | 202 | 2 | cmp time 5 |  | 300 | uint16 | Read/Write | Time interval for Data status = 4
| 40359 | 358 | 166 | 16 | 1 | 204 | 2 | cmp time 6 |  | 600 | uint16 | Read/Write | Time interval for Data status = 5
| 40360 | 359 | 167 | 16 | 1 | 206 | 2 | cmp time 7 |  | 900 | uint16 | Read/Write | Time interval for Data status = 6
| 40361 | 360 | 168 | 16 | 1 | 208 | 2 | cmp time 8 |  | 1800 | uint16 | Read/Write | Time interval for Data status = 7
| 40362 | 361 | 169 | 16 | 1 | 210 | 2 | cmp time 9 |  | 3600 | uint16 | Read/Write | Time interval for Data status = 8
SETTING TIMEOUT VALUE OF RF TIMEOUT COUNT | 40363 | 362 | 16A | 16 | 1 | 212 | 2 | timeout_count_threshold |  | 630 | uint16 | Read/Write | Time interval for Rf_timeout_count increase one more
| 40364 | 363 | 16B | 16 | 36 | 214 | 72 | spare |  |  |  | Read/Write
DEVICE INFO | 40001 | 0 | 0 | 3 | 2 | 0 | 4 | device info |  | STC1 | string | Read | Wireless sensor co-ordinator
| 40003 | 2 | 2 | 3 | 4 | 4 | 8 | firmware version |  | 1.7 | string | Read
| 40007 | 6 | 6 | 3 | 2 | 12 | 4 | hardware version |  | 2 | string | Read
Note:
+ update_enable_reg = 0xB601 (bit_0) = 46593 => update Cycle_wakeup, cycle_healthstatus of node (sensors)
+ update_enable_reg = 0xB680 (bit_7) = 46720 => update Data_numblock, data_reg, data_numreg of node
+ update_enable_reg = 0xB640 (bit_6) = 46656 => update Offset temp, humidity, pressure, analog value; update pulse width for digital input
+ update_enable_reg = 0xB620 (bit_5) = 46624 => update Delta temp, humidity, pressure
+ update_enable_reg = 0xB610 (bit_4) = 46608 => update CT for WS433-AC
+ update_enable_reg = 0xB608 (bit_3) = 46600 => update Cut-off for WS433-AC
+ update_enable_reg = 0xB604 (bit_2) = 46596 => spare
+ update_enable_reg = 0xB602 (bit_1) = 46594 => update High_Threshold_1,Low_Threshold_1,High_Threshold_2,Low_Threshold_2
+ password = 190577
READ: Func 03
WRITE: Func 16

## Chi tiết (hidden)
Modbus Register | # of register | Adr | Size | Description | Range | Default | Format | Property | Comment
0 | 2 | 0 | 4 | device info |  | STC1 | string | Read | Sensor tag receiver
2 | 4 | 4 | 8 | firmware version |  | 1.6 | string | Read
6 | 2 | 12 | 4 | hardware version |  | 2 | string | Read
8 | 1 | 16 | 2 | rssi node 1 & rssi node 2 |  |  | int8 | Read | rssi thực tế = rssi node - 256 (dBm)
9 | 1 | 18 | 2 | rssi node 3 & rssi node 4 |  |  | int8 | Read
10 | 1 | 20 | 2 | rssi node 5 & rssi node 6 |  |  | int8 | Read
11 | 1 | 22 | 2 | rssi node 7 & rssi node 8 |  |  | int8 | Read
12 | 1 | 24 | 2 | rssi node 9 & rssi node 10 |  |  | int8 | Read
13 | 1 | 26 | 2 | rssi node 11 & rssi node 12 |  |  | int8 | Read
14 | 1 | 28 | 2 | rssi node 13 & rssi node 14 |  |  | int8 | Read
15 | 1 | 30 | 2 | rssi node 15 & rssi node 16 |  |  | int8 | Read
16 | 1 | 32 | 2 | rssi node 17 & rssi node 18 |  |  | int8 | Read
17 | 1 | 34 | 2 | rssi node 19 & rssi node 20 |  |  | int8 | Read
18 | 1 | 36 | 2 | rssi node 21 & rssi node 22 |  |  | int8 | Read
19 | 1 | 38 | 2 | rssi node 23 & rssi node 24 |  |  | int8 | Read
20 | 1 | 40 | 2 | rssi node 25 & rssi node 26 |  |  | int8 | Read
21 | 1 | 42 | 2 | rssi node 27 & rssi node 28 |  |  | int8 | Read
22 | 1 | 44 | 2 | rssi node 29 & rssi node 30 |  |  | int8 | Read
23 | 1 | 46 | 2 | rssi node 31 & rssi node 32 |  |  | int8 | Read
24 | 1 | 48 | 2 | rssi node 33 & rssi node 34 |  |  | int8 | Read
25 | 1 | 50 | 2 | rssi node 35 & rssi node 36 |  |  | int8 | Read
26 | 1 | 52 | 2 | rssi node 37 & rssi node 38 |  |  | int8 | Read
27 | 1 | 54 | 2 | rssi node 39 & rssi node 40 |  |  | int8 | Read
28 | 1 | 56 | 2 | data status node 1 & data status node 2 | 0-9, 99 |  | uint8 | Read | + n = thời gian từ lúc nhận được data mới nhất của sensor đến hiện tại + data status = 99: khi chưa nhận được bất kỳ data nào 0: khi n <= cmp time 1 1: khi cmp time 1 < n <= cmp time 2 2: khi cmp time 2 < n <= cmp time 3 3: khi cmp time 3 < n <= cmp time 4 4: khi cmp time 4 < n <= cmp time 5 5: khi cmp time 5 < n <= cmp time 6 6: khi cmp time 6 < n <= cmp time 7 7: khi cmp time 7 < n <= cmp time 8 8: khi cmp time 8 < n <= cmp time 9 9: khi cmp time n > cmp time 9
29 | 1 | 58 | 2 | data status node 3 & data status node 4 | 0-9, 99 |  | uint8 | Read
30 | 1 | 60 | 2 | data status node 5 & data status node 6 | 0-9, 99 |  | uint8 | Read
31 | 1 | 62 | 2 | data status node 7 & data status node 8 | 0-9, 99 |  | uint8 | Read
32 | 1 | 64 | 2 | data status node 9 & data status node 10 | 0-9, 99 |  | uint8 | Read
33 | 1 | 66 | 2 | data status node 11 & data status node 12 | 0-9, 99 |  | uint8 | Read
34 | 1 | 68 | 2 | data status node 13 & data status node 14 | 0-9, 99 |  | uint8 | Read
35 | 1 | 70 | 2 | data status node 15 & data status node 16 | 0-9, 99 |  | uint8 | Read
36 | 1 | 72 | 2 | data status node 17 & data status node 18 | 0-9, 99 |  | uint8 | Read
37 | 1 | 74 | 2 | data status node 19 & data status node 20 | 0-9, 99 |  | uint8 | Read
38 | 1 | 76 | 2 | data status node 21 & data status node 22 | 0-9, 99 |  | uint8 | Read
39 | 1 | 78 | 2 | data status node 23 & data status node 24 | 0-9, 99 |  | uint8 | Read
40 | 1 | 80 | 2 | data status node 25 & data status node 26 | 0-9, 99 |  | uint8 | Read
41 | 1 | 82 | 2 | data status node 27 & data status node 28 | 0-9, 99 |  | uint8 | Read
42 | 1 | 84 | 2 | data status node 29 & data status node 30 | 0-9, 99 |  | uint8 | Read
43 | 1 | 86 | 2 | data status node 31 & data status node 32 | 0-9, 99 |  | uint8 | Read
44 | 1 | 88 | 2 | data status node 33 & data status node 34 | 0-9, 99 |  | uint8 | Read
45 | 1 | 90 | 2 | data status node 35 & data status node 36 | 0-9, 99 |  | uint8 | Read
46 | 1 | 92 | 2 | data status node 37 & data status node 38 | 0-9, 99 |  | uint8 | Read
47 | 1 | 94 | 2 | data status node 39 & data status node 40 | 0-9, 99 |  | uint8 | Read
48 | 1 | 96 | 2 | rf timeout count node 1 & rf timeout count node 2 |  |  | uint8 | Read | Tăng thêm 1 khi data status >=3
49 | 1 | 98 | 2 | rf timeout count node 3 & rf timeout count node 4 |  |  | uint8 | Read
50 | 1 | 100 | 2 | rf timeout count node 5 & rf timeout count node 6 |  |  | uint8 | Read
51 | 1 | 102 | 2 | rf timeout count node 7 & rf timeout count node 8 |  |  | uint8 | Read
52 | 1 | 104 | 2 | rf timeout count node 9 & rf timeout count node 10 |  |  | uint8 | Read
53 | 1 | 106 | 2 | rf timeout count node 11 & rf timeout count node 12 |  |  | uint8 | Read
54 | 1 | 108 | 2 | rf timeout count node 13 & rf timeout count node 14 |  |  | uint8 | Read
55 | 1 | 110 | 2 | rf timeout count node 15 & rf timeout count node 16 |  |  | uint8 | Read
56 | 1 | 112 | 2 | rf timeout count node 17 & rf timeout count node 18 |  |  | uint8 | Read
57 | 1 | 114 | 2 | rf timeout count node 19 & rf timeout count node 20 |  |  | uint8 | Read
58 | 1 | 116 | 2 | rf timeout count node 21 & rf timeout count node 22 |  |  | uint8 | Read
59 | 1 | 118 | 2 | rf timeout count node 23 & rf timeout count node 24 |  |  | uint8 | Read
60 | 1 | 120 | 2 | rf timeout count node 25 & rf timeout count node 26 |  |  | uint8 | Read
61 | 1 | 122 | 2 | rf timeout count node 27 & rf timeout count node 28 |  |  | uint8 | Read
62 | 1 | 124 | 2 | rf timeout count node 29 & rf timeout count node 30 |  |  | uint8 | Read
63 | 1 | 126 | 2 | rf timeout count node 31 & rf timeout count node 32 |  |  | uint8 | Read
64 | 1 | 128 | 2 | rf timeout count node 33 & rf timeout count node 34 |  |  | uint8 | Read
65 | 1 | 130 | 2 | rf timeout count node 35 & rf timeout count node 36 |  |  | uint8 | Read
66 | 1 | 132 | 2 | rf timeout count node 37 & rf timeout count node 38 |  |  | uint8 | Read
67 | 1 | 134 | 2 | rf timeout count node 39 & rf timeout count node 40 |  |  | uint8 | Read
68 | 1 | 136 | 2 | rssi status node 1 & rssi status node 2 | 0-4 |  | uint8 | Read | + RSSI = 0..-54dBm => RSSI Status = 4 (sóng RF mạnh nhất) + RSSI = -55..-69dBm => RSSI Status = 3 + RSSI = -70..-79dBm => RSSI Status = 2 + RSSI = -80..-100dBm => RSSI Status = 1 + RSSI < -100dBm => RSSI Status = 0
69 | 1 | 138 | 2 | rssi status node 3 & rssi status node 4 | 0-4 |  | uint8 | Read
70 | 1 | 140 | 2 | rssi status node 5 & rssi status node 6 | 0-4 |  | uint8 | Read
71 | 1 | 142 | 2 | rssi status node 7 & rssi status node 8 | 0-4 |  | uint8 | Read
72 | 1 | 144 | 2 | rssi status node 9 & rssi status node 10 | 0-4 |  | uint8 | Read
73 | 1 | 146 | 2 | rssi status node 11 & rssi status node 12 | 0-4 |  | uint8 | Read
74 | 1 | 148 | 2 | rssi status node 13 & rssi status node 14 | 0-4 |  | uint8 | Read
75 | 1 | 150 | 2 | rssi status node 15 & rssi status node 16 | 0-4 |  | uint8 | Read
76 | 1 | 152 | 2 | rssi status node 17 & rssi status node 18 | 0-4 |  | uint8 | Read
77 | 1 | 154 | 2 | rssi status node 19 & rssi status node 20 | 0-4 |  | uint8 | Read
78 | 1 | 156 | 2 | rssi status node 21 & rssi status node 22 | 0-4 |  | uint8 | Read
79 | 1 | 158 | 2 | rssi status node 23 & rssi status node 24 | 0-4 |  | uint8 | Read
80 | 1 | 160 | 2 | rssi status node 25 & rssi status node 26 | 0-4 |  | uint8 | Read
81 | 1 | 162 | 2 | rssi status node 27 & rssi status node 28 | 0-4 |  | uint8 | Read
82 | 1 | 164 | 2 | rssi status node 29 & rssi status node 30 | 0-4 |  | uint8 | Read
83 | 1 | 166 | 2 | rssi status node 31 & rssi status node 32 | 0-4 |  | uint8 | Read
84 | 1 | 168 | 2 | rssi status node 33 & rssi status node 34 | 0-4 |  | uint8 | Read
85 | 1 | 170 | 2 | rssi status node 35 & rssi status node 36 | 0-4 |  | uint8 | Read
86 | 1 | 172 | 2 | rssi status node 37 & rssi status node 38 | 0-4 |  | uint8 | Read
87 | 1 | 174 | 2 | rssi status node 39 & rssi status node 40 | 0-4 |  | uint8 | Read
88 | 60 | 176 | 120 | spare |  |  | uint8 | Read
148 | 1 | 296 | 2 | rx seq node 1 & rx seq node 2 |  |  | uint8 | Read
149 | 1 | 298 | 2 | rx seq node 3 & rx seq node 4 |  |  | uint8 | Read
150 | 1 | 300 | 2 | rx seq node 5 & rx seq node 6 |  |  | uint8 | Read
151 | 1 | 302 | 2 | rx seq node 7 & rx seq node 8 |  |  | uint8 | Read
152 | 1 | 304 | 2 | rx seq node 9 & rx seq node 10 |  |  | uint8 | Read
153 | 1 | 306 | 2 | rx seq node 11 & rx seq node 12 |  |  | uint8 | Read
154 | 1 | 308 | 2 | rx seq node 13 & rx seq node 14 |  |  | uint8 | Read
155 | 1 | 310 | 2 | rx seq node 15 & rx seq node 16 |  |  | uint8 | Read
156 | 1 | 312 | 2 | rx seq node 17 & rx seq node 18 |  |  | uint8 | Read
157 | 1 | 314 | 2 | rx seq node 19 & rx seq node 20 |  |  | uint8 | Read
158 | 1 | 316 | 2 | rx seq node 21 & rx seq node 22 |  |  | uint8 | Read
159 | 1 | 318 | 2 | rx seq node 23 & rx seq node 24 |  |  | uint8 | Read
160 | 1 | 320 | 2 | rx seq node 25 & rx seq node 26 |  |  | uint8 | Read
161 | 1 | 322 | 2 | rx seq node 27 & rx seq node 28 |  |  | uint8 | Read
162 | 1 | 324 | 2 | rx seq node 29 & rx seq node 30 |  |  | uint8 | Read
163 | 1 | 326 | 2 | rx seq node 31 & rx seq node 32 |  |  | uint8 | Read
164 | 1 | 328 | 2 | rx seq node 33 & rx seq node 34 |  |  | uint8 | Read
165 | 1 | 330 | 2 | rx seq node 35 & rx seq node 36 |  |  | uint8 | Read
166 | 1 | 332 | 2 | rx seq node 37 & rx seq node 38 |  |  | uint8 | Read
167 | 1 | 334 | 2 | rx seq node 39 & rx seq node 40 |  |  | uint8 | Read
168 | 1 | 336 | 2 | rx duplication count node 1 & rx duplication count node 2 |  |  | uint8 | Read
169 | 1 | 338 | 2 | rx duplication count node 3 & rx duplication count node 4 |  |  | uint8 | Read
170 | 1 | 340 | 2 | rx duplication count node 5 & rx duplication count node 6 |  |  | uint8 | Read
171 | 1 | 342 | 2 | rx duplication count node 7 & rx duplication count node 8 |  |  | uint8 | Read
172 | 1 | 344 | 2 | rx duplication count node 9 & rx duplication count node 10 |  |  | uint8 | Read
173 | 1 | 346 | 2 | rx duplication count node 11 & rx duplication count node 12 |  |  | uint8 | Read
174 | 1 | 348 | 2 | rx duplication count node 13 & rx duplication count node 14 |  |  | uint8 | Read
175 | 1 | 350 | 2 | rx duplication count node 15 & rx duplication count node 16 |  |  | uint8 | Read
176 | 1 | 352 | 2 | rx duplication count node 17 & rx duplication count node 18 |  |  | uint8 | Read
177 | 1 | 354 | 2 | rx duplication count node 19 & rx duplication count node 20 |  |  | uint8 | Read
178 | 1 | 356 | 2 | rx duplication count node 21 & rx duplication count node 22 |  |  | uint8 | Read
179 | 1 | 358 | 2 | rx duplication count node 23 & rx duplication count node 24 |  |  | uint8 | Read
180 | 1 | 360 | 2 | rx duplication count node 25 & rx duplication count node 26 |  |  | uint8 | Read
181 | 1 | 362 | 2 | rx duplication count node 27 & rx duplication count node 28 |  |  | uint8 | Read
182 | 1 | 364 | 2 | rx duplication count node 29 & rx duplication count node 30 |  |  | uint8 | Read
183 | 1 | 366 | 2 | rx duplication count node 31 & rx duplication count node 32 |  |  | uint8 | Read
184 | 1 | 368 | 2 | rx duplication count node 33 & rx duplication count node 34 |  |  | uint8 | Read
185 | 1 | 370 | 2 | rx duplication count node 35 & rx duplication count node 36 |  |  | uint8 | Read
186 | 1 | 372 | 2 | rx duplication count node 37 & rx duplication count node 38 |  |  | uint8 | Read
187 | 1 | 374 | 2 | rx duplication count node 39 & rx duplication count node 40 |  |  | uint8 | Read
188 | 1 | 376 | 2 | sync status node 1 & sync status node 2 | 0-2, 99 |  | uint8 | Read | 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
189 | 1 | 378 | 2 | sync status node 3 & sync status node 4 | 0-2, 99 |  | uint8 | Read
190 | 1 | 380 | 2 | sync status node 5 & sync status node 6 | 0-2, 99 |  | uint8 | Read
191 | 1 | 382 | 2 | sync status node 7 & sync status node 8 | 0-2, 99 |  | uint8 | Read
192 | 1 | 384 | 2 | sync status node 9 & sync status node 10 | 0-2, 99 |  | uint8 | Read
193 | 1 | 386 | 2 | sync status node 11 & sync status node 12 | 0-2, 99 |  | uint8 | Read
194 | 1 | 388 | 2 | sync status node 13 & sync status node 14 | 0-2, 99 |  | uint8 | Read
195 | 1 | 390 | 2 | sync status node 15 & sync status node 16 | 0-2, 99 |  | uint8 | Read
196 | 1 | 392 | 2 | sync status node 17 & sync status node 18 | 0-2, 99 |  | uint8 | Read
197 | 1 | 394 | 2 | sync status node 19 & sync status node 20 | 0-2, 99 |  | uint8 | Read
198 | 1 | 396 | 2 | sync status node 21 & sync status node 22 | 0-2, 99 |  | uint8 | Read
199 | 1 | 398 | 2 | sync status node 23 & sync status node 24 | 0-2, 99 |  | uint8 | Read
200 | 1 | 400 | 2 | sync status node 25 & sync status node 26 | 0-2, 99 |  | uint8 | Read
201 | 1 | 402 | 2 | sync status node 27 & sync status node 28 | 0-2, 99 |  | uint8 | Read
202 | 1 | 404 | 2 | sync status node 29 & sync status node 30 | 0-2, 99 |  | uint8 | Read
203 | 1 | 406 | 2 | sync status node 31 & sync status node 32 | 0-2, 99 |  | uint8 | Read
204 | 1 | 408 | 2 | sync status node 33 & sync status node 34 | 0-2, 99 |  | uint8 | Read
205 | 1 | 410 | 2 | sync status node 35 & sync status node 36 | 0-2, 99 |  | uint8 | Read
206 | 1 | 412 | 2 | sync status node 37 & sync status node 38 | 0-2, 99 |  | uint8 | Read
207 | 1 | 414 | 2 | sync status node 39 & sync status node 40 | 0-2, 99 |  | uint8 | Read
41216 | 32 |  | 64 | Data area of Node 1 |  |  |  | Read | 0xA100..0xA120
41472 | 32 |  | 64 | Data area of Node 2 |  |  |  | Read | 0xA200..0xA220
41728 | 32 |  | 64 | Data area of Node 3 |  |  |  | Read | 0xA300..0xA320
41984 | 32 |  | 64 | Data area of Node 4 |  |  |  | Read | 0xA400..0xA420
42240 | 32 |  | 64 | Data area of Node 5 |  |  |  | Read | 0xA500..0xA520
42496 | 32 |  | 64 | Data area of Node 6 |  |  |  | Read | 0xA600..0xA620
42752 | 32 |  | 64 | Data area of Node 7 |  |  |  | Read | 0xA700..0xA720
43008 | 32 |  | 64 | Data area of Node 8 |  |  |  | Read | 0xA800..0xA820
43264 | 32 |  | 64 | Data area of Node 9 |  |  |  | Read | 0xA900..0xA920
43520 | 32 |  | 64 | Data area of Node 10 |  |  |  | Read | 0xAA00..0xAA20
45312 | 32 |  | 64 | Data area of Node 11 |  |  |  | Read | 0xB100..0xB120
45568 | 32 |  | 64 | Data area of Node 12 |  |  |  | Read | 0xB200..0xB220
45824 | 32 |  | 64 | Data area of Node 13 |  |  |  | Read | 0xB300..0xB320
46080 | 32 |  | 64 | Data area of Node 14 |  |  |  | Read | 0xB400..0xB420
46336 | 32 |  | 64 | Data area of Node 15 |  |  |  | Read | 0xB500..0xB520
46592 | 32 |  | 64 | Data area of Node 16 |  |  |  | Read | 0xB600..0xB620
46848 | 32 |  | 64 | Data area of Node 17 |  |  |  | Read | 0xB700..0xB720
47104 | 32 |  | 64 | Data area of Node 18 |  |  |  | Read | 0xB800..0xB820
47360 | 32 |  | 64 | Data area of Node 19 |  |  |  | Read | 0xB900..0xB920
47616 | 32 |  | 64 | Data area of Node 20 |  |  |  | Read | 0xBA00..0xBA20
49408 | 32 |  | 64 | Data area of Node 21 |  |  |  | Read | 0xC100..0xC120
49664 | 32 |  | 64 | Data area of Node 22 |  |  |  | Read | 0xC200..0xC220
49920 | 32 |  | 64 | Data area of Node 23 |  |  |  | Read | 0xC300..0xC320
50176 | 32 |  | 64 | Data area of Node 24 |  |  |  | Read | 0xC400..0xC420
50432 | 32 |  | 64 | Data area of Node 25 |  |  |  | Read | 0xC500..0xC520
50688 | 32 |  | 64 | Data area of Node 26 |  |  |  | Read | 0xC600..0xC620
50944 | 32 |  | 64 | Data area of Node 27 |  |  |  | Read | 0xC700..0xC720
51200 | 32 |  | 64 | Data area of Node 28 |  |  |  | Read | 0xC800..0xC820
51456 | 32 |  | 64 | Data area of Node 29 |  |  |  | Read | 0xC900..0xC920
51712 | 32 |  | 64 | Data area of Node 30 |  |  |  | Read | 0xCA00..0xCA20
53504 | 32 |  | 64 | Data area of Node 31 |  |  |  | Read | 0xD100..0xD120
53760 | 32 |  | 64 | Data area of Node 32 |  |  |  | Read | 0xD200..0xD220
54016 | 32 |  | 64 | Data area of Node 33 |  |  |  | Read | 0xD300..0xD320
54272 | 32 |  | 64 | Data area of Node 34 |  |  |  | Read | 0xD400..0xD420
54528 | 32 |  | 64 | Data area of Node 35 |  |  |  | Read | 0xD500..0xD520
54784 | 32 |  | 64 | Data area of Node 36 |  |  |  | Read | 0xD600..0xD620
55040 | 32 |  | 64 | Data area of Node 37 |  |  |  | Read | 0xD700..0xD720
55296 | 32 |  | 64 | Data area of Node 38 |  |  |  | Read | 0xD800..0xD820
55552 | 32 |  | 64 | Data area of Node 39 |  |  |  | Read | 0xD900..0xD920
55808 | 32 |  | 64 | Data area of Node 40 |  |  |  | Read | 0xDA00..0xDA20
256 | 1 | 0 | 2 | modbus address | 1-247 | 1 | uint16 | Read/Write
257 | 1 | 2 | 2 | modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
258 | 1 | 4 | 2 | modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
259 | 9 | 6 | 18 | serial number |  |  | string | Read/Write(PW)
268 | 2 | 24 | 4 | password for setting |  |  | uint32 | Read/Write | Password = 190577
270 | 2 | 28 | 4 | receiver id |  |  | uint32 | Read/Write(PW)
272 | 1 | 32 | 2 | num of node | 0-40 |  | uint16 | Read/Write
273 | 2 | 34 | 4 | node id 1 |  |  | uint32 | Read/Write
275 | 2 | 38 | 4 | node id 2 |  |  | uint32 | Read/Write
277 | 2 | 42 | 4 | node id 3 |  |  | uint32 | Read/Write
279 | 2 | 46 | 4 | node id 4 |  |  | uint32 | Read/Write
281 | 2 | 50 | 4 | node id 5 |  |  | uint32 | Read/Write
283 | 2 | 54 | 4 | node id 6 |  |  | uint32 | Read/Write
285 | 2 | 58 | 4 | node id 7 |  |  | uint32 | Read/Write
287 | 2 | 62 | 4 | node id 8 |  |  | uint32 | Read/Write
289 | 2 | 66 | 4 | node id 9 |  |  | uint32 | Read/Write
291 | 2 | 70 | 4 | node id 10 |  |  | uint32 | Read/Write
293 | 2 | 74 | 4 | node id 11 |  |  | uint32 | Read/Write
295 | 2 | 78 | 4 | node id 12 |  |  | uint32 | Read/Write
297 | 2 | 82 | 4 | node id 13 |  |  | uint32 | Read/Write
299 | 2 | 86 | 4 | node id 14 |  |  | uint32 | Read/Write
301 | 2 | 90 | 4 | node id 15 |  |  | uint32 | Read/Write
303 | 2 | 94 | 4 | node id 16 |  |  | uint32 | Read/Write
305 | 2 | 98 | 4 | node id 17 |  |  | uint32 | Read/Write
307 | 2 | 102 | 4 | node id 18 |  |  | uint32 | Read/Write
309 | 2 | 106 | 4 | node id 19 |  |  | uint32 | Read/Write
311 | 2 | 110 | 4 | node id 20 |  |  | uint32 | Read/Write
313 | 2 | 114 | 4 | node id 21 |  |  | uint32 | Read/Write
315 | 2 | 118 | 4 | node id 22 |  |  | uint32 | Read/Write
317 | 2 | 122 | 4 | node id 23 |  |  | uint32 | Read/Write
319 | 2 | 126 | 4 | node id 24 |  |  | uint32 | Read/Write
321 | 2 | 130 | 4 | node id 25 |  |  | uint32 | Read/Write
323 | 2 | 134 | 4 | node id 26 |  |  | uint32 | Read/Write
325 | 2 | 138 | 4 | node id 27 |  |  | uint32 | Read/Write
327 | 2 | 142 | 4 | node id 28 |  |  | uint32 | Read/Write
329 | 2 | 146 | 4 | node id 29 |  |  | uint32 | Read/Write
331 | 2 | 150 | 4 | node id 30 |  |  | uint32 | Read/Write
333 | 2 | 154 | 4 | node id 31 |  |  | uint32 | Read/Write
335 | 2 | 158 | 4 | node id 32 |  |  | uint32 | Read/Write
337 | 2 | 162 | 4 | node id 33 |  |  | uint32 | Read/Write
339 | 2 | 166 | 4 | node id 34 |  |  | uint32 | Read/Write
341 | 2 | 170 | 4 | node id 35 |  |  | uint32 | Read/Write
343 | 2 | 174 | 4 | node id 36 |  |  | uint32 | Read/Write
345 | 2 | 178 | 4 | node id 37 |  |  | uint32 | Read/Write
347 | 2 | 182 | 4 | node id 38 |  |  | uint32 | Read/Write
349 | 2 | 186 | 4 | node id 39 |  |  | uint32 | Read/Write
351 | 2 | 190 | 4 | node id 40 |  |  | uint32 | Read/Write
353 | 1 | 194 | 2 | cmp time 1 |  | 15 | uint16 | Read/Write | second
354 | 1 | 196 | 2 | cmp time 2 |  | 30 | uint16 | Read/Write | second
355 | 1 | 198 | 2 | cmp time 3 |  | 45 | uint16 | Read/Write | second
356 | 1 | 200 | 2 | cmp time 4 |  | 60 | uint16 | Read/Write | second
357 | 1 | 202 | 2 | cmp time 5 |  | 300 | uint16 | Read/Write | second
358 | 1 | 204 | 2 | cmp time 6 |  | 600 | uint16 | Read/Write | second
359 | 1 | 206 | 2 | cmp time 7 |  | 900 | uint16 | Read/Write | second
360 | 1 | 208 | 2 | cmp time 8 |  | 1800 | uint16 | Read/Write | second
361 | 1 | 210 | 2 | cmp time 9 |  | 3600 | uint16 | Read/Write | second
362 | 37 | 212 | 74 | spare
399 | 1 | 286 | 2 | sync all node | 0-1 |  | uint16 | Read/Write | 1: restart sync
400 | 1 | 288 | 2 | Update_enable_Node1 |  |  | hex | Read/Write | + update enable = 0xB601 = 46593 => update Cycle_wakeup, cycle_healthstatus of node + update enable = 0xB680 = 46720 => update Data_numblock, data_reg, data_numreg of node + update enable = 0xB640 = 46656 => update Offset temp, humidity, pulse width 4 channel of node + update enable = 0xB620 = 46624 => update Delta temp, humidity, counter of node
401 | 1 | 290 | 2 | Cycle_wakeup_Node1 |  |  | uint16 | Read/Write
402 | 1 | 292 | 2 | Cycle_heathsta_Node1 |  |  | uint16 | Read/Write
403 | 1 | 294 | 2 | Data_numblock_Node1 |  |  | uint16 | Read/Write
404 | 1 | 296 | 2 | Data_reg 1_Node1 |  |  | uint16 | Read/Write
405 | 1 | 298 | 2 | Data_numreg 1_Node1 |  |  | uint16 | Read/Write
406 | 1 | 300 | 2 | Data_reg 2_Node1 |  |  | uint16 | Read/Write
407 | 1 | 302 | 2 | Data_numReg 2_Node1 |  |  | uint16 | Read/Write
408 | 1 | 304 | 2 | Data_reg 3_Node1 |  |  | uint16 | Read/Write
409 | 1 | 306 | 2 | Data_numReg 3_Node1 |  |  | uint16 | Read/Write
410 | 20 | 308 | 40 | Reserve_regs_Node1 |  |  |  | Read/Write | reserve registers for node 1= 20 regs = 40 bytes
430 | 1 | 348 | 2 | Update_enable_Node2 |  |  | hex | Read/Write
431 | 1 | 350 | 2 | Cycle_wakeup_Node2 |  |  | uint16 | Read/Write
432 | 1 | 352 | 2 | Cycle_heathsta_Node2 |  |  | uint16 | Read/Write
433 | 1 | 354 | 2 | Data_numblock_Node2 |  |  | uint16 | Read/Write
434 | 1 | 356 | 2 | Data_reg 1_Node2 |  |  | uint16 | Read/Write
435 | 1 | 358 | 2 | Data_numreg 1_Node2 |  |  | uint16 | Read/Write
436 | 1 | 360 | 2 | Data_reg 2_Node2 |  |  | uint16 | Read/Write
437 | 1 | 362 | 2 | Data_numReg 2_Node2 |  |  | uint16 | Read/Write
438 | 1 | 364 | 2 | Data_reg 3_Node2 |  |  | uint16 | Read/Write
439 | 1 | 366 | 2 | Data_numReg 3_Node2 |  |  | uint16 | Read/Write
440 | 20 | 368 | 40 | Reserve_regs_Node2 |  |  |  | Read/Write | reserve registers for node 2 = 20 regs = 40 bytes
460 | 1 | 408 | 2 | Update_enable_Node3 |  |  | hex | Read/Write
461 | 1 | 410 | 2 | Cycle_wakeup_Node3 |  |  | uint16 | Read/Write
462 | 1 | 412 | 2 | Cycle_heathsta_Node3 |  |  | uint16 | Read/Write
463 | 1 | 414 | 2 | Data_numblock_Node3 |  |  | uint16 | Read/Write
464 | 1 | 416 | 2 | Data_reg 1_Node3 |  |  | uint16 | Read/Write
465 | 1 | 418 | 2 | Data_numreg 1_Node3 |  |  | uint16 | Read/Write
466 | 1 | 420 | 2 | Data_reg 2_Node3 |  |  | uint16 | Read/Write
467 | 1 | 422 | 2 | Data_numReg 2_Node3 |  |  | uint16 | Read/Write
468 | 1 | 424 | 2 | Data_reg 3_Node3 |  |  | uint16 | Read/Write
469 | 1 | 426 | 2 | Data_numReg 3_Node3 |  |  | uint16 | Read/Write
470 | 20 | 428 | 40 | Reserve_regs_Node3 |  |  |  | Read/Write | reserve registers for node 3 = 20 regs = 40 bytes
490 | 1 | 468 | 2 | Update_enable_Node4 |  |  | hex | Read/Write
491 | 1 | 470 | 2 | Cycle_wakeup_Node4 |  |  | uint16 | Read/Write
492 | 1 | 472 | 2 | Cycle_heathsta_Node4 |  |  | uint16 | Read/Write
493 | 1 | 474 | 2 | Data_numblock_Node4 |  |  | uint16 | Read/Write
494 | 1 | 476 | 2 | Data_reg 1_Node4 |  |  | uint16 | Read/Write
495 | 1 | 478 | 2 | Data_numreg 1_Node4 |  |  | uint16 | Read/Write
496 | 1 | 480 | 2 | Data_reg 2_Node4 |  |  | uint16 | Read/Write
497 | 1 | 482 | 2 | Data_numReg 2_Node4 |  |  | uint16 | Read/Write
498 | 1 | 484 | 2 | Data_reg 3_Node4 |  |  | uint16 | Read/Write
499 | 1 | 486 | 2 | Data_numReg 3_Node4 |  |  | uint16 | Read/Write
500 | 20 | 488 | 40 | Reserve_regs_Node4 |  |  |  | Read/Write | reserve registers for node 4 = 20 regs = 40 bytes
520 | 1 | 528 | 2 | Update_enable_Node5 |  |  | hex | Read/Write
521 | 1 | 530 | 2 | Cycle_wakeup_Node5 |  |  | uint16 | Read/Write
522 | 1 | 532 | 2 | Cycle_heathsta_Node5 |  |  | uint16 | Read/Write
523 | 1 | 534 | 2 | Data_numblock_Node5 |  |  | uint16 | Read/Write
524 | 1 | 536 | 2 | Data_reg 1_Node5 |  |  | uint16 | Read/Write
525 | 1 | 538 | 2 | Data_numreg 1_Node5 |  |  | uint16 | Read/Write
526 | 1 | 540 | 2 | Data_reg 2_Node5 |  |  | uint16 | Read/Write
527 | 1 | 542 | 2 | Data_numReg 2_Node5 |  |  | uint16 | Read/Write
528 | 1 | 544 | 2 | Data_reg 3_Node5 |  |  | uint16 | Read/Write
529 | 1 | 546 | 2 | Data_numReg 3_Node5 |  |  | uint16 | Read/Write
530 | 20 | 548 | 40 | Reserve_regs_Node5 |  |  |  | Read/Write | reserve registers for node 5 = 20 regs = 40 bytes
550 | 1 | 588 | 2 | Update_enable_Node6 |  |  | hex | Read/Write
551 | 1 | 590 | 2 | Cycle_wakeup_Node6 |  |  | uint16 | Read/Write
552 | 1 | 592 | 2 | Cycle_heathsta_Node6 |  |  | uint16 | Read/Write
553 | 1 | 594 | 2 | Data_numblock_Node6 |  |  | uint16 | Read/Write
554 | 1 | 596 | 2 | Data_reg 1_Node6 |  |  | uint16 | Read/Write
555 | 1 | 598 | 2 | Data_numreg 1_Node6 |  |  | uint16 | Read/Write
556 | 1 | 600 | 2 | Data_reg 2_Node6 |  |  | uint16 | Read/Write
557 | 1 | 602 | 2 | Data_numReg 2_Node6 |  |  | uint16 | Read/Write
558 | 1 | 604 | 2 | Data_reg 3_Node6 |  |  | uint16 | Read/Write
559 | 1 | 606 | 2 | Data_numReg 3_Node6 |  |  | uint16 | Read/Write
560 | 20 | 608 | 40 | Reserve_regs_Node6 |  |  |  | Read/Write | reserve registers for node 6 = 20 regs = 40 bytes
580 | 1 | 648 | 2 | Update_enable_Node7 |  |  | hex | Read/Write
581 | 1 | 650 | 2 | Cycle_wakeup_Node7 |  |  | uint16 | Read/Write
582 | 1 | 652 | 2 | Cycle_heathsta_Node7 |  |  | uint16 | Read/Write
583 | 1 | 654 | 2 | Data_numblock_Node7 |  |  | uint16 | Read/Write
584 | 1 | 656 | 2 | Data_reg 1_Node7 |  |  | uint16 | Read/Write
585 | 1 | 658 | 2 | Data_numreg 1_Node7 |  |  | uint16 | Read/Write
586 | 1 | 660 | 2 | Data_reg 2_Node7 |  |  | uint16 | Read/Write
587 | 1 | 662 | 2 | Data_numReg 2_Node7 |  |  | uint16 | Read/Write
588 | 1 | 664 | 2 | Data_reg 3_Node7 |  |  | uint16 | Read/Write
589 | 1 | 666 | 2 | Data_numReg 3_Node7 |  |  | uint16 | Read/Write
590 | 20 | 668 | 40 | Reserve_regs_Node7 |  |  |  | Read/Write | reserve registers for node 7 = 20 regs = 40 bytes
610 | 1 | 708 | 2 | Update_enable_Node8 |  |  | hex | Read/Write
611 | 1 | 710 | 2 | Cycle_wakeup_Node8 |  |  | uint16 | Read/Write
612 | 1 | 712 | 2 | Cycle_heathsta_Node8 |  |  | uint16 | Read/Write
613 | 1 | 714 | 2 | Data_numblock_Node8 |  |  | uint16 | Read/Write
614 | 1 | 716 | 2 | Data_reg 1_Node8 |  |  | uint16 | Read/Write
615 | 1 | 718 | 2 | Data_numreg 1_Node8 |  |  | uint16 | Read/Write
616 | 1 | 720 | 2 | Data_reg 2_Node8 |  |  | uint16 | Read/Write
617 | 1 | 722 | 2 | Data_numReg 2_Node8 |  |  | uint16 | Read/Write
618 | 1 | 724 | 2 | Data_reg 3_Node8 |  |  | uint16 | Read/Write
619 | 1 | 726 | 2 | Data_numReg 3_Node8 |  |  | uint16 | Read/Write
620 | 20 | 728 | 40 | Reserve_regs_Node8 |  |  |  | Read/Write | reserve registers for node 8 = 20 regs = 40 bytes
640 | 1 | 768 | 2 | Update_enable_Node9 |  |  | hex | Read/Write
641 | 1 | 770 | 2 | Cycle_wakeup_Node9 |  |  | uint16 | Read/Write
642 | 1 | 772 | 2 | Cycle_heathsta_Node9 |  |  | uint16 | Read/Write
643 | 1 | 774 | 2 | Data_numblock_Node9 |  |  | uint16 | Read/Write
644 | 1 | 776 | 2 | Data_reg 1_Node9 |  |  | uint16 | Read/Write
645 | 1 | 778 | 2 | Data_numreg 1_Node9 |  |  | uint16 | Read/Write
646 | 1 | 780 | 2 | Data_reg 2_Node9 |  |  | uint16 | Read/Write
647 | 1 | 782 | 2 | Data_numReg 2_Node9 |  |  | uint16 | Read/Write
648 | 1 | 784 | 2 | Data_reg 3_Node9 |  |  | uint16 | Read/Write
649 | 1 | 786 | 2 | Data_numReg 3_Node9 |  |  | uint16 | Read/Write
650 | 20 | 788 | 40 | Reserve_regs_Node9 |  |  |  | Read/Write | reserve registers for node 9 = 20 regs = 40 bytes
670 | 1 | 828 | 2 | Update_enable_Node10 |  |  | hex | Read/Write
671 | 1 | 830 | 2 | Cycle_wakeup_Node10 |  |  | uint16 | Read/Write
672 | 1 | 832 | 2 | Cycle_heathsta_Node10 |  |  | uint16 | Read/Write
673 | 1 | 834 | 2 | Data_numblock_Node10 |  |  | uint16 | Read/Write
674 | 1 | 836 | 2 | Data_reg 1_Node10 |  |  | uint16 | Read/Write
675 | 1 | 838 | 2 | Data_numreg 1_Node10 |  |  | uint16 | Read/Write
676 | 1 | 840 | 2 | Data_reg 2_Node10 |  |  | uint16 | Read/Write
677 | 1 | 842 | 2 | Data_numReg 2_Node10 |  |  | uint16 | Read/Write
678 | 1 | 844 | 2 | Data_reg 3_Node10 |  |  | uint16 | Read/Write
679 | 1 | 846 | 2 | Data_numReg 3_Node10 |  |  | uint16 | Read/Write
680 | 20 | 848 | 40 | Reserve_regs_Node10 |  |  |  | Read/Write | reserve registers for node 10 = 20 regs = 40 bytes
700 | 1 | 888 | 2 | Update_enable_Node11 |  |  | hex | Read/Write
701 | 1 | 890 | 2 | Cycle_wakeup_Node11 |  |  | uint16 | Read/Write
702 | 1 | 892 | 2 | Cycle_heathsta_Node11 |  |  | uint16 | Read/Write
703 | 1 | 894 | 2 | Data_numblock_Node11 |  |  | uint16 | Read/Write
704 | 1 | 896 | 2 | Data_reg 1_Node11 |  |  | uint16 | Read/Write
705 | 1 | 898 | 2 | Data_numreg 1_Node11 |  |  | uint16 | Read/Write
706 | 1 | 900 | 2 | Data_reg 2_Node11 |  |  | uint16 | Read/Write
707 | 1 | 902 | 2 | Data_numReg 2_Node11 |  |  | uint16 | Read/Write
708 | 1 | 904 | 2 | Data_reg 3_Node11 |  |  | uint16 | Read/Write
709 | 1 | 906 | 2 | Data_numReg 3_Node11 |  |  | uint16 | Read/Write
710 | 20 | 908 | 40 | Reserve_regs_Node11 |  |  |  | Read/Write | reserve registers for node 11 = 20 regs = 40 bytes
730 | 1 | 948 | 2 | Update_enable_Node12 |  |  | hex | Read/Write
731 | 1 | 950 | 2 | Cycle_wakeup_Node12 |  |  | uint16 | Read/Write
732 | 1 | 952 | 2 | Cycle_heathsta_Node12 |  |  | uint16 | Read/Write
733 | 1 | 954 | 2 | Data_numblock_Node12 |  |  | uint16 | Read/Write
734 | 1 | 956 | 2 | Data_reg 1_Node12 |  |  | uint16 | Read/Write
735 | 1 | 958 | 2 | Data_numreg 1_Node12 |  |  | uint16 | Read/Write
736 | 1 | 960 | 2 | Data_reg 2_Node12 |  |  | uint16 | Read/Write
737 | 1 | 962 | 2 | Data_numReg 2_Node12 |  |  | uint16 | Read/Write
738 | 1 | 964 | 2 | Data_reg 3_Node12 |  |  | uint16 | Read/Write
739 | 1 | 966 | 2 | Data_numReg 3_Node12 |  |  | uint16 | Read/Write
740 | 20 | 968 | 40 | Reserve_regs_Node12 |  |  |  | Read/Write | reserve registers for node 12 = 20 regs = 40 bytes
760 | 1 | 1008 | 2 | Update_enable_Node13 |  |  | hex | Read/Write
761 | 1 | 1010 | 2 | Cycle_wakeup_Node13 |  |  | uint16 | Read/Write
762 | 1 | 1012 | 2 | Cycle_heathsta_Node13 |  |  | uint16 | Read/Write
763 | 1 | 1014 | 2 | Data_numblock_Node13 |  |  | uint16 | Read/Write
764 | 1 | 1016 | 2 | Data_reg 1_Node13 |  |  | uint16 | Read/Write
765 | 1 | 1018 | 2 | Data_numreg 1_Node13 |  |  | uint16 | Read/Write
766 | 1 | 1020 | 2 | Data_reg 2_Node13 |  |  | uint16 | Read/Write
767 | 1 | 1022 | 2 | Data_numReg 2_Node13 |  |  | uint16 | Read/Write
768 | 1 | 1024 | 2 | Data_reg 3_Node13 |  |  | uint16 | Read/Write
769 | 1 | 1026 | 2 | Data_numReg 3_Node13 |  |  | uint16 | Read/Write
770 | 20 | 1028 | 40 | Reserve_regs_Node13 |  |  |  | Read/Write | reserve registers for node 13 = 20 regs = 40 bytes
790 | 1 | 1068 | 2 | Update_enable_Node14 |  |  | hex | Read/Write
791 | 1 | 1070 | 2 | Cycle_wakeup_Node14 |  |  | uint16 | Read/Write
792 | 1 | 1072 | 2 | Cycle_heathsta_Node14 |  |  | uint16 | Read/Write
793 | 1 | 1074 | 2 | Data_numblock_Node14 |  |  | uint16 | Read/Write
794 | 1 | 1076 | 2 | Data_reg 1_Node14 |  |  | uint16 | Read/Write
795 | 1 | 1078 | 2 | Data_numreg 1_Node14 |  |  | uint16 | Read/Write
796 | 1 | 1080 | 2 | Data_reg 2_Node14 |  |  | uint16 | Read/Write
797 | 1 | 1082 | 2 | Data_numReg 2_Node14 |  |  | uint16 | Read/Write
798 | 1 | 1084 | 2 | Data_reg 3_Node14 |  |  | uint16 | Read/Write
799 | 1 | 1086 | 2 | Data_numReg 3_Node14 |  |  | uint16 | Read/Write
800 | 20 | 1088 | 40 | Reserve_regs_Node14 |  |  |  | Read/Write | reserve registers for node 14 = 20 regs = 40 bytes
820 | 1 | 1128 | 2 | Update_enable_Node15 |  |  | hex | Read/Write
821 | 1 | 1130 | 2 | Cycle_wakeup_Node15 |  |  | uint16 | Read/Write
822 | 1 | 1132 | 2 | Cycle_heathsta_Node15 |  |  | uint16 | Read/Write
823 | 1 | 1134 | 2 | Data_numblock_Node15 |  |  | uint16 | Read/Write
824 | 1 | 1136 | 2 | Data_reg 1_Node15 |  |  | uint16 | Read/Write
825 | 1 | 1138 | 2 | Data_numreg 1_Node15 |  |  | uint16 | Read/Write
826 | 1 | 1140 | 2 | Data_reg 2_Node15 |  |  | uint16 | Read/Write
827 | 1 | 1142 | 2 | Data_numReg 2_Node15 |  |  | uint16 | Read/Write
828 | 1 | 1144 | 2 | Data_reg 3_Node15 |  |  | uint16 | Read/Write
829 | 1 | 1146 | 2 | Data_numReg 3_Node15 |  |  | uint16 | Read/Write
830 | 20 | 1148 | 40 | Reserve_regs_Node15 |  |  |  | Read/Write | reserve registers for node 15 = 20 regs = 40 bytes
850 | 1 | 1188 | 2 | Update_enable_Node16 |  |  | hex | Read/Write
851 | 1 | 1190 | 2 | Cycle_wakeup_Node16 |  |  | uint16 | Read/Write
852 | 1 | 1192 | 2 | Cycle_heathsta_Node16 |  |  | uint16 | Read/Write
853 | 1 | 1194 | 2 | Data_numblock_Node16 |  |  | uint16 | Read/Write
854 | 1 | 1196 | 2 | Data_reg 1_Node16 |  |  | uint16 | Read/Write
855 | 1 | 1198 | 2 | Data_numreg 1_Node16 |  |  | uint16 | Read/Write
856 | 1 | 1200 | 2 | Data_reg 2_Node16 |  |  | uint16 | Read/Write
857 | 1 | 1202 | 2 | Data_numReg 2_Node16 |  |  | uint16 | Read/Write
858 | 1 | 1204 | 2 | Data_reg 3_Node16 |  |  | uint16 | Read/Write
859 | 1 | 1206 | 2 | Data_numReg 3_Node16 |  |  | uint16 | Read/Write
860 | 20 | 1208 | 40 | Reserve_regs_Node16 |  |  |  | Read/Write | reserve registers for node 16 = 20 regs = 40 bytes
880 | 1 | 1248 | 2 | Update_enable_Node17 |  |  | hex | Read/Write
881 | 1 | 1250 | 2 | Cycle_wakeup_Node17 |  |  | uint16 | Read/Write
882 | 1 | 1252 | 2 | Cycle_heathsta_Node17 |  |  | uint16 | Read/Write
883 | 1 | 1254 | 2 | Data_numblock_Node17 |  |  | uint16 | Read/Write
884 | 1 | 1256 | 2 | Data_reg 1_Node17 |  |  | uint16 | Read/Write
885 | 1 | 1258 | 2 | Data_numreg 1_Node17 |  |  | uint16 | Read/Write
886 | 1 | 1260 | 2 | Data_reg 2_Node17 |  |  | uint16 | Read/Write
887 | 1 | 1262 | 2 | Data_numReg 2_Node17 |  |  | uint16 | Read/Write
888 | 1 | 1264 | 2 | Data_reg 3_Node17 |  |  | uint16 | Read/Write
889 | 1 | 1266 | 2 | Data_numReg 3_Node17 |  |  | uint16 | Read/Write
890 | 20 | 1268 | 40 | Reserve_regs_Node17 |  |  |  | Read/Write | reserve registers for node 17 = 20 regs = 40 bytes
910 | 1 | 1308 | 2 | Update_enable_Node18 |  |  | hex | Read/Write
911 | 1 | 1310 | 2 | Cycle_wakeup_Node18 |  |  | uint16 | Read/Write
912 | 1 | 1312 | 2 | Cycle_heathsta_Node18 |  |  | uint16 | Read/Write
913 | 1 | 1314 | 2 | Data_numblock_Node18 |  |  | uint16 | Read/Write
914 | 1 | 1316 | 2 | Data_reg 1_Node18 |  |  | uint16 | Read/Write
915 | 1 | 1318 | 2 | Data_numreg 1_Node18 |  |  | uint16 | Read/Write
916 | 1 | 1320 | 2 | Data_reg 2_Node18 |  |  | uint16 | Read/Write
917 | 1 | 1322 | 2 | Data_numReg 2_Node18 |  |  | uint16 | Read/Write
918 | 1 | 1324 | 2 | Data_reg 3_Node18 |  |  | uint16 | Read/Write
919 | 1 | 1326 | 2 | Data_numReg 3_Node18 |  |  | uint16 | Read/Write
920 | 20 | 1328 | 40 | Reserve_regs_Node18 |  |  |  | Read/Write | reserve registers for node 18 = 20 regs = 40 bytes
940 | 1 | 1368 | 2 | Update_enable_Node19 |  |  | hex | Read/Write
941 | 1 | 1370 | 2 | Cycle_wakeup_Node19 |  |  | uint16 | Read/Write
942 | 1 | 1372 | 2 | Cycle_heathsta_Node19 |  |  | uint16 | Read/Write
943 | 1 | 1374 | 2 | Data_numblock_Node19 |  |  | uint16 | Read/Write
944 | 1 | 1376 | 2 | Data_reg 1_Node19 |  |  | uint16 | Read/Write
945 | 1 | 1378 | 2 | Data_numreg 1_Node19 |  |  | uint16 | Read/Write
946 | 1 | 1380 | 2 | Data_reg 2_Node19 |  |  | uint16 | Read/Write
947 | 1 | 1382 | 2 | Data_numReg 2_Node19 |  |  | uint16 | Read/Write
948 | 1 | 1384 | 2 | Data_reg 3_Node19 |  |  | uint16 | Read/Write
949 | 1 | 1386 | 2 | Data_numReg 3_Node19 |  |  | uint16 | Read/Write
950 | 20 | 1388 | 40 | Reserve_regs_Node19 |  |  |  | Read/Write | reserve registers for node 19 = 20 regs = 40 bytes
970 | 1 | 1428 | 2 | Update_enable_Node20 |  |  | hex | Read/Write
971 | 1 | 1430 | 2 | Cycle_wakeup_Node20 |  |  | uint16 | Read/Write
972 | 1 | 1432 | 2 | Cycle_heathsta_Node20 |  |  | uint16 | Read/Write
973 | 1 | 1434 | 2 | Data_numblock_Node20 |  |  | uint16 | Read/Write
974 | 1 | 1436 | 2 | Data_reg 1_Node20 |  |  | uint16 | Read/Write
975 | 1 | 1438 | 2 | Data_numreg 1_Node20 |  |  | uint16 | Read/Write
976 | 1 | 1440 | 2 | Data_reg 2_Node20 |  |  | uint16 | Read/Write
977 | 1 | 1442 | 2 | Data_numReg 2_Node20 |  |  | uint16 | Read/Write
978 | 1 | 1444 | 2 | Data_reg 3_Node20 |  |  | uint16 | Read/Write
979 | 1 | 1446 | 2 | Data_numReg 3_Node20 |  |  | uint16 | Read/Write
980 | 20 | 1448 | 40 | Reserve_regs_Node20 |  |  |  | Read/Write | reserve registers for node 20 = 20 regs = 40 bytes
1000 | 1 | 1488 | 2 | Update_enable_Node21 |  |  | hex | Read/Write
1001 | 1 | 1490 | 2 | Cycle_wakeup_Node21 |  |  | uint16 | Read/Write
1002 | 1 | 1492 | 2 | Cycle_heathsta_Node21 |  |  | uint16 | Read/Write
1003 | 1 | 1494 | 2 | Data_numblock_Node21 |  |  | uint16 | Read/Write
1004 | 1 | 1496 | 2 | Data_reg 1_Node21 |  |  | uint16 | Read/Write
1005 | 1 | 1498 | 2 | Data_numreg 1_Node21 |  |  | uint16 | Read/Write
1006 | 1 | 1500 | 2 | Data_reg 2_Node21 |  |  | uint16 | Read/Write
1007 | 1 | 1502 | 2 | Data_numReg 2_Node21 |  |  | uint16 | Read/Write
1008 | 1 | 1504 | 2 | Data_reg 3_Node21 |  |  | uint16 | Read/Write
1009 | 1 | 1506 | 2 | Data_numReg 3_Node21 |  |  | uint16 | Read/Write
1010 | 20 | 1508 | 40 | Reserve_regs_Node21 |  |  |  | Read/Write | reserve registers for node 21 = 20 regs = 40 bytes
1030 | 1 | 1548 | 2 | Update_enable_Node22 |  |  | hex | Read/Write
1031 | 1 | 1550 | 2 | Cycle_wakeup_Node22 |  |  | uint16 | Read/Write
1032 | 1 | 1552 | 2 | Cycle_heathsta_Node22 |  |  | uint16 | Read/Write
1033 | 1 | 1554 | 2 | Data_numblock_Node22 |  |  | uint16 | Read/Write
1034 | 1 | 1556 | 2 | Data_reg 1_Node22 |  |  | uint16 | Read/Write
1035 | 1 | 1558 | 2 | Data_numreg 1_Node22 |  |  | uint16 | Read/Write
1036 | 1 | 1560 | 2 | Data_reg 2_Node22 |  |  | uint16 | Read/Write
1037 | 1 | 1562 | 2 | Data_numReg 2_Node22 |  |  | uint16 | Read/Write
1038 | 1 | 1564 | 2 | Data_reg 3_Node22 |  |  | uint16 | Read/Write
1039 | 1 | 1566 | 2 | Data_numReg 3_Node22 |  |  | uint16 | Read/Write
1040 | 20 | 1568 | 40 | Reserve_regs_Node22 |  |  |  | Read/Write | reserve registers for node 22 = 20 regs = 40 bytes
1060 | 1 | 1608 | 2 | Update_enable_Node23 |  |  | hex | Read/Write
1061 | 1 | 1610 | 2 | Cycle_wakeup_Node23 |  |  | uint16 | Read/Write
1062 | 1 | 1612 | 2 | Cycle_heathsta_Node23 |  |  | uint16 | Read/Write
1063 | 1 | 1614 | 2 | Data_numblock_Node23 |  |  | uint16 | Read/Write
1064 | 1 | 1616 | 2 | Data_reg 1_Node23 |  |  | uint16 | Read/Write
1065 | 1 | 1618 | 2 | Data_numreg 1_Node23 |  |  | uint16 | Read/Write
1066 | 1 | 1620 | 2 | Data_reg 2_Node23 |  |  | uint16 | Read/Write
1067 | 1 | 1622 | 2 | Data_numReg 2_Node23 |  |  | uint16 | Read/Write
1068 | 1 | 1624 | 2 | Data_reg 3_Node23 |  |  | uint16 | Read/Write
1069 | 1 | 1626 | 2 | Data_numReg 3_Node23 |  |  | uint16 | Read/Write
1070 | 20 | 1628 | 40 | Reserve_regs_Node23 |  |  |  | Read/Write | reserve registers for node 23 = 20 regs = 40 bytes
1090 | 1 | 1668 | 2 | Update_enable_Node24 |  |  | hex | Read/Write
1091 | 1 | 1670 | 2 | Cycle_wakeup_Node24 |  |  | uint16 | Read/Write
1092 | 1 | 1672 | 2 | Cycle_heathsta_Node24 |  |  | uint16 | Read/Write
1093 | 1 | 1674 | 2 | Data_numblock_Node24 |  |  | uint16 | Read/Write
1094 | 1 | 1676 | 2 | Data_reg 1_Node24 |  |  | uint16 | Read/Write
1095 | 1 | 1678 | 2 | Data_numreg 1_Node24 |  |  | uint16 | Read/Write
1096 | 1 | 1680 | 2 | Data_reg 2_Node24 |  |  | uint16 | Read/Write
1097 | 1 | 1682 | 2 | Data_numReg 2_Node24 |  |  | uint16 | Read/Write
1098 | 1 | 1684 | 2 | Data_reg 3_Node24 |  |  | uint16 | Read/Write
1099 | 1 | 1686 | 2 | Data_numReg 3_Node24 |  |  | uint16 | Read/Write
1100 | 20 | 1688 | 40 | Reserve_regs_Node24 |  |  |  | Read/Write | reserve registers for node 24 = 20 regs = 40 bytes
1120 | 1 | 1728 | 2 | Update_enable_Node25 |  |  | hex | Read/Write
1121 | 1 | 1730 | 2 | Cycle_wakeup_Node25 |  |  | uint16 | Read/Write
1122 | 1 | 1732 | 2 | Cycle_heathsta_Node25 |  |  | uint16 | Read/Write
1123 | 1 | 1734 | 2 | Data_numblock_Node25 |  |  | uint16 | Read/Write
1124 | 1 | 1736 | 2 | Data_reg 1_Node25 |  |  | uint16 | Read/Write
1125 | 1 | 1738 | 2 | Data_numreg 1_Node25 |  |  | uint16 | Read/Write
1126 | 1 | 1740 | 2 | Data_reg 2_Node25 |  |  | uint16 | Read/Write
1127 | 1 | 1742 | 2 | Data_numReg 2_Node25 |  |  | uint16 | Read/Write
1128 | 1 | 1744 | 2 | Data_reg 3_Node25 |  |  | uint16 | Read/Write
1129 | 1 | 1746 | 2 | Data_numReg 3_Node25 |  |  | uint16 | Read/Write
1130 | 20 | 1748 | 40 | Reserve_regs_Node25 |  |  |  | Read/Write | reserve registers for node 25 = 20 regs = 40 bytes
1150 | 1 | 1788 | 2 | Update_enable_Node26 |  |  | hex | Read/Write
1151 | 1 | 1790 | 2 | Cycle_wakeup_Node26 |  |  | uint16 | Read/Write
1152 | 1 | 1792 | 2 | Cycle_heathsta_Node26 |  |  | uint16 | Read/Write
1153 | 1 | 1794 | 2 | Data_numblock_Node26 |  |  | uint16 | Read/Write
1154 | 1 | 1796 | 2 | Data_reg 1_Node26 |  |  | uint16 | Read/Write
1155 | 1 | 1798 | 2 | Data_numreg 1_Node26 |  |  | uint16 | Read/Write
1156 | 1 | 1800 | 2 | Data_reg 2_Node26 |  |  | uint16 | Read/Write
1157 | 1 | 1802 | 2 | Data_numReg 2_Node26 |  |  | uint16 | Read/Write
1158 | 1 | 1804 | 2 | Data_reg 3_Node26 |  |  | uint16 | Read/Write
1159 | 1 | 1806 | 2 | Data_numReg 3_Node26 |  |  | uint16 | Read/Write
1160 | 20 | 1808 | 40 | Reserve_regs_Node26 |  |  |  | Read/Write | reserve registers for node 26 = 20 regs = 40 bytes
1180 | 1 | 1848 | 2 | Update_enable_Node27 |  |  | hex | Read/Write
1181 | 1 | 1850 | 2 | Cycle_wakeup_Node27 |  |  | uint16 | Read/Write
1182 | 1 | 1852 | 2 | Cycle_heathsta_Node27 |  |  | uint16 | Read/Write
1183 | 1 | 1854 | 2 | Data_numblock_Node27 |  |  | uint16 | Read/Write
1184 | 1 | 1856 | 2 | Data_reg 1_Node27 |  |  | uint16 | Read/Write
1185 | 1 | 1858 | 2 | Data_numreg 1_Node27 |  |  | uint16 | Read/Write
1186 | 1 | 1860 | 2 | Data_reg 2_Node27 |  |  | uint16 | Read/Write
1187 | 1 | 1862 | 2 | Data_numReg 2_Node27 |  |  | uint16 | Read/Write
1188 | 1 | 1864 | 2 | Data_reg 3_Node27 |  |  | uint16 | Read/Write
1189 | 1 | 1866 | 2 | Data_numReg 3_Node27 |  |  | uint16 | Read/Write
1190 | 20 | 1868 | 40 | Reserve_regs_Node27 |  |  |  | Read/Write | reserve registers for node 27 = 20 regs = 40 bytes
1210 | 1 | 1908 | 2 | Update_enable_Node28 |  |  | hex | Read/Write
1211 | 1 | 1910 | 2 | Cycle_wakeup_Node28 |  |  | uint16 | Read/Write
1212 | 1 | 1912 | 2 | Cycle_heathsta_Node28 |  |  | uint16 | Read/Write
1213 | 1 | 1914 | 2 | Data_numblock_Node28 |  |  | uint16 | Read/Write
1214 | 1 | 1916 | 2 | Data_reg 1_Node28 |  |  | uint16 | Read/Write
1215 | 1 | 1918 | 2 | Data_numreg 1_Node28 |  |  | uint16 | Read/Write
1216 | 1 | 1920 | 2 | Data_reg 2_Node28 |  |  | uint16 | Read/Write
1217 | 1 | 1922 | 2 | Data_numReg 2_Node28 |  |  | uint16 | Read/Write
1218 | 1 | 1924 | 2 | Data_reg 3_Node28 |  |  | uint16 | Read/Write
1219 | 1 | 1926 | 2 | Data_numReg 3_Node28 |  |  | uint16 | Read/Write
1220 | 20 | 1928 | 40 | Reserve_regs_Node28 |  |  |  | Read/Write | reserve registers for node 28 = 20 regs = 40 bytes
1240 | 1 | 1968 | 2 | Update_enable_Node29 |  |  | hex | Read/Write
1241 | 1 | 1970 | 2 | Cycle_wakeup_Node29 |  |  | uint16 | Read/Write
1242 | 1 | 1972 | 2 | Cycle_heathsta_Node29 |  |  | uint16 | Read/Write
1243 | 1 | 1974 | 2 | Data_numblock_Node29 |  |  | uint16 | Read/Write
1244 | 1 | 1976 | 2 | Data_reg 1_Node29 |  |  | uint16 | Read/Write
1245 | 1 | 1978 | 2 | Data_numreg 1_Node29 |  |  | uint16 | Read/Write
1246 | 1 | 1980 | 2 | Data_reg 2_Node29 |  |  | uint16 | Read/Write
1247 | 1 | 1982 | 2 | Data_numReg 2_Node29 |  |  | uint16 | Read/Write
1248 | 1 | 1984 | 2 | Data_reg 3_Node29 |  |  | uint16 | Read/Write
1249 | 1 | 1986 | 2 | Data_numReg 3_Node29 |  |  | uint16 | Read/Write
1250 | 20 | 1988 | 40 | Reserve_regs_Node29 |  |  |  | Read/Write | reserve registers for node 29 = 20 regs = 40 bytes
1270 | 1 | 2028 | 2 | Update_enable_Node30 |  |  | hex | Read/Write
1271 | 1 | 2030 | 2 | Cycle_wakeup_Node30 |  |  | uint16 | Read/Write
1272 | 1 | 2032 | 2 | Cycle_heathsta_Node30 |  |  | uint16 | Read/Write
1273 | 1 | 2034 | 2 | Data_numblock_Node30 |  |  | uint16 | Read/Write
1274 | 1 | 2036 | 2 | Data_reg 1_Node30 |  |  | uint16 | Read/Write
1275 | 1 | 2038 | 2 | Data_numreg 1_Node30 |  |  | uint16 | Read/Write
1276 | 1 | 2040 | 2 | Data_reg 2_Node30 |  |  | uint16 | Read/Write
1277 | 1 | 2042 | 2 | Data_numReg 2_Node30 |  |  | uint16 | Read/Write
1278 | 1 | 2044 | 2 | Data_reg 3_Node30 |  |  | uint16 | Read/Write
1279 | 1 | 2046 | 2 | Data_numReg 3_Node30 |  |  | uint16 | Read/Write
1280 | 20 | 2048 | 40 | Reserve_regs_Node30 |  |  |  | Read/Write | reserve registers for node 30 = 20 regs = 40 bytes
1300 | 1 | 2088 | 2 | Update_enable_Node31 |  |  | hex | Read/Write
1301 | 1 | 2090 | 2 | Cycle_wakeup_Node31 |  |  | uint16 | Read/Write
1302 | 1 | 2092 | 2 | Cycle_heathsta_Node31 |  |  | uint16 | Read/Write
1303 | 1 | 2094 | 2 | Data_numblock_Node31 |  |  | uint16 | Read/Write
1304 | 1 | 2096 | 2 | Data_reg 1_Node31 |  |  | uint16 | Read/Write
1305 | 1 | 2098 | 2 | Data_numreg 1_Node31 |  |  | uint16 | Read/Write
1306 | 1 | 2100 | 2 | Data_reg 2_Node31 |  |  | uint16 | Read/Write
1307 | 1 | 2102 | 2 | Data_numReg 2_Node31 |  |  | uint16 | Read/Write
1308 | 1 | 2104 | 2 | Data_reg 3_Node31 |  |  | uint16 | Read/Write
1309 | 1 | 2106 | 2 | Data_numReg 3_Node31 |  |  | uint16 | Read/Write
1310 | 20 | 2108 | 40 | Reserve_regs_Node31 |  |  |  | Read/Write | reserve registers for node 31= 20 regs = 40 bytes
1330 | 1 | 2148 | 2 | Update_enable_Node32 |  |  | hex | Read/Write
1331 | 1 | 2150 | 2 | Cycle_wakeup_Node32 |  |  | uint16 | Read/Write
1332 | 1 | 2152 | 2 | Cycle_heathsta_Node32 |  |  | uint16 | Read/Write
1333 | 1 | 2154 | 2 | Data_numblock_Node32 |  |  | uint16 | Read/Write
1334 | 1 | 2156 | 2 | Data_reg 1_Node32 |  |  | uint16 | Read/Write
1335 | 1 | 2158 | 2 | Data_numreg 1_Node32 |  |  | uint16 | Read/Write
1336 | 1 | 2160 | 2 | Data_reg 2_Node32 |  |  | uint16 | Read/Write
1337 | 1 | 2162 | 2 | Data_numReg 2_Node32 |  |  | uint16 | Read/Write
1338 | 1 | 2164 | 2 | Data_reg 3_Node32 |  |  | uint16 | Read/Write
1339 | 1 | 2166 | 2 | Data_numReg 3_Node32 |  |  | uint16 | Read/Write
1340 | 20 | 2168 | 40 | Reserve_regs_Node32 |  |  |  | Read/Write | reserve registers for node 32 = 20 regs = 40 bytes
1360 | 1 | 2208 | 2 | Update_enable_Node33 |  |  | hex | Read/Write
1361 | 1 | 2210 | 2 | Cycle_wakeup_Node33 |  |  | uint16 | Read/Write
1362 | 1 | 2212 | 2 | Cycle_heathsta_Node33 |  |  | uint16 | Read/Write
1363 | 1 | 2214 | 2 | Data_numblock_Node33 |  |  | uint16 | Read/Write
1364 | 1 | 2216 | 2 | Data_reg 1_Node33 |  |  | uint16 | Read/Write
1365 | 1 | 2218 | 2 | Data_numreg 1_Node33 |  |  | uint16 | Read/Write
1366 | 1 | 2220 | 2 | Data_reg 2_Node33 |  |  | uint16 | Read/Write
1367 | 1 | 2222 | 2 | Data_numReg 2_Node33 |  |  | uint16 | Read/Write
1368 | 1 | 2224 | 2 | Data_reg 3_Node33 |  |  | uint16 | Read/Write
1369 | 1 | 2226 | 2 | Data_numReg 3_Node33 |  |  | uint16 | Read/Write
1370 | 20 | 2228 | 40 | Reserve_regs_Node33 |  |  |  | Read/Write | reserve registers for node 33 = 20 regs = 40 bytes
1390 | 1 | 2268 | 2 | Update_enable_Node34 |  |  | hex | Read/Write
1391 | 1 | 2270 | 2 | Cycle_wakeup_Node34 |  |  | uint16 | Read/Write
1392 | 1 | 2272 | 2 | Cycle_heathsta_Node34 |  |  | uint16 | Read/Write
1393 | 1 | 2274 | 2 | Data_numblock_Node34 |  |  | uint16 | Read/Write
1394 | 1 | 2276 | 2 | Data_reg 1_Node34 |  |  | uint16 | Read/Write
1395 | 1 | 2278 | 2 | Data_numreg 1_Node34 |  |  | uint16 | Read/Write
1396 | 1 | 2280 | 2 | Data_reg 2_Node34 |  |  | uint16 | Read/Write
1397 | 1 | 2282 | 2 | Data_numReg 2_Node34 |  |  | uint16 | Read/Write
1398 | 1 | 2284 | 2 | Data_reg 3_Node34 |  |  | uint16 | Read/Write
1399 | 1 | 2286 | 2 | Data_numReg 3_Node34 |  |  | uint16 | Read/Write
1400 | 20 | 2288 | 40 | Reserve_regs_Node34 |  |  |  | Read/Write | reserve registers for node 34 = 20 regs = 40 bytes
1420 | 1 | 2328 | 2 | Update_enable_Node35 |  |  | hex | Read/Write
1421 | 1 | 2330 | 2 | Cycle_wakeup_Node35 |  |  | uint16 | Read/Write
1422 | 1 | 2332 | 2 | Cycle_heathsta_Node35 |  |  | uint16 | Read/Write
1423 | 1 | 2334 | 2 | Data_numblock_Node35 |  |  | uint16 | Read/Write
1424 | 1 | 2336 | 2 | Data_reg 1_Node35 |  |  | uint16 | Read/Write
1425 | 1 | 2338 | 2 | Data_numreg 1_Node35 |  |  | uint16 | Read/Write
1426 | 1 | 2340 | 2 | Data_reg 2_Node35 |  |  | uint16 | Read/Write
1427 | 1 | 2342 | 2 | Data_numReg 2_Node35 |  |  | uint16 | Read/Write
1428 | 1 | 2344 | 2 | Data_reg 3_Node35 |  |  | uint16 | Read/Write
1429 | 1 | 2346 | 2 | Data_numReg 3_Node35 |  |  | uint16 | Read/Write
1430 | 20 | 2348 | 40 | Reserve_regs_Node35 |  |  |  | Read/Write | reserve registers for node 35 = 20 regs = 40 bytes
1450 | 1 | 2388 | 2 | Update_enable_Node36 |  |  | hex | Read/Write
1451 | 1 | 2390 | 2 | Cycle_wakeup_Node36 |  |  | uint16 | Read/Write
1452 | 1 | 2392 | 2 | Cycle_heathsta_Node36 |  |  | uint16 | Read/Write
1453 | 1 | 2394 | 2 | Data_numblock_Node36 |  |  | uint16 | Read/Write
1454 | 1 | 2396 | 2 | Data_reg 1_Node36 |  |  | uint16 | Read/Write
1455 | 1 | 2398 | 2 | Data_numreg 1_Node36 |  |  | uint16 | Read/Write
1456 | 1 | 2400 | 2 | Data_reg 2_Node36 |  |  | uint16 | Read/Write
1457 | 1 | 2402 | 2 | Data_numReg 2_Node36 |  |  | uint16 | Read/Write
1458 | 1 | 2404 | 2 | Data_reg 3_Node36 |  |  | uint16 | Read/Write
1459 | 1 | 2406 | 2 | Data_numReg 3_Node36 |  |  | uint16 | Read/Write
1460 | 20 | 2408 | 40 | Reserve_regs_Node36 |  |  |  | Read/Write | reserve registers for node 36 = 20 regs = 40 bytes
1480 | 1 | 2448 | 2 | Update_enable_Node37 |  |  | hex | Read/Write
1481 | 1 | 2450 | 2 | Cycle_wakeup_Node37 |  |  | uint16 | Read/Write
1482 | 1 | 2452 | 2 | Cycle_heathsta_Node37 |  |  | uint16 | Read/Write
1483 | 1 | 2454 | 2 | Data_numblock_Node37 |  |  | uint16 | Read/Write
1484 | 1 | 2456 | 2 | Data_reg 1_Node37 |  |  | uint16 | Read/Write
1485 | 1 | 2458 | 2 | Data_numreg 1_Node37 |  |  | uint16 | Read/Write
1486 | 1 | 2460 | 2 | Data_reg 2_Node37 |  |  | uint16 | Read/Write
1487 | 1 | 2462 | 2 | Data_numReg 2_Node37 |  |  | uint16 | Read/Write
1488 | 1 | 2464 | 2 | Data_reg 3_Node37 |  |  | uint16 | Read/Write
1489 | 1 | 2466 | 2 | Data_numReg 3_Node37 |  |  | uint16 | Read/Write
1490 | 20 | 2468 | 40 | Reserve_regs_Node37 |  |  |  | Read/Write | reserve registers for node 37 = 20 regs = 40 bytes
1510 | 1 | 2508 | 2 | Update_enable_Node38 |  |  | hex | Read/Write
1511 | 1 | 2510 | 2 | Cycle_wakeup_Node38 |  |  | uint16 | Read/Write
1512 | 1 | 2512 | 2 | Cycle_heathsta_Node38 |  |  | uint16 | Read/Write
1513 | 1 | 2514 | 2 | Data_numblock_Node38 |  |  | uint16 | Read/Write
1514 | 1 | 2516 | 2 | Data_reg 1_Node38 |  |  | uint16 | Read/Write
1515 | 1 | 2518 | 2 | Data_numreg 1_Node38 |  |  | uint16 | Read/Write
1516 | 1 | 2520 | 2 | Data_reg 2_Node38 |  |  | uint16 | Read/Write
1517 | 1 | 2522 | 2 | Data_numReg 2_Node38 |  |  | uint16 | Read/Write
1518 | 1 | 2524 | 2 | Data_reg 3_Node38 |  |  | uint16 | Read/Write
1519 | 1 | 2526 | 2 | Data_numReg 3_Node38 |  |  | uint16 | Read/Write
1520 | 20 | 2528 | 40 | Reserve_regs_Node38 |  |  |  | Read/Write | reserve registers for node 38 = 20 regs = 40 bytes
1540 | 1 | 2568 | 2 | Update_enable_Node39 |  |  | hex | Read/Write
1541 | 1 | 2570 | 2 | Cycle_wakeup_Node39 |  |  | uint16 | Read/Write
1542 | 1 | 2572 | 2 | Cycle_heathsta_Node39 |  |  | uint16 | Read/Write
1543 | 1 | 2574 | 2 | Data_numblock_Node39 |  |  | uint16 | Read/Write
1544 | 1 | 2576 | 2 | Data_reg 1_Node39 |  |  | uint16 | Read/Write
1545 | 1 | 2578 | 2 | Data_numreg 1_Node39 |  |  | uint16 | Read/Write
1546 | 1 | 2580 | 2 | Data_reg 2_Node39 |  |  | uint16 | Read/Write
1547 | 1 | 2582 | 2 | Data_numReg 2_Node39 |  |  | uint16 | Read/Write
1548 | 1 | 2584 | 2 | Data_reg 3_Node39 |  |  | uint16 | Read/Write
1549 | 1 | 2586 | 2 | Data_numReg 3_Node39 |  |  | uint16 | Read/Write
1550 | 20 | 2588 | 40 | Reserve_regs_Node39 |  |  |  | Read/Write | reserve registers for node 39 = 20 regs = 40 bytes
1570 | 1 | 2628 | 2 | Update_enable_Node40 |  |  | hex | Read/Write
1571 | 1 | 2630 | 2 | Cycle_wakeup_Node40 |  |  | uint16 | Read/Write
1572 | 1 | 2632 | 2 | Cycle_heathsta_Node40 |  |  | uint16 | Read/Write
1573 | 1 | 2634 | 2 | Data_numblock_Node40 |  |  | uint16 | Read/Write
1574 | 1 | 2636 | 2 | Data_reg 1_Node40 |  |  | uint16 | Read/Write
1575 | 1 | 2638 | 2 | Data_numreg 1_Node40 |  |  | uint16 | Read/Write
1576 | 1 | 2640 | 2 | Data_reg 2_Node40 |  |  | uint16 | Read/Write
1577 | 1 | 2642 | 2 | Data_numReg 2_Node40 |  |  | uint16 | Read/Write
1578 | 1 | 2644 | 2 | Data_reg 3_Node40 |  |  | uint16 | Read/Write
1579 | 1 | 2646 | 2 | Data_numReg 3_Node40 |  |  | uint16 | Read/Write
1580 | 20 | 2648 | 40 | Reserve_regs_Node40 |  |  |  | Read/Write | reserve registers for node 40 = 20 regs = 40 bytes
Note:
+ update_enable_reg = 0xB601 = 46593 => update Cycle_wakeup, cycle_healthstatus of node (sensors)
+ update_enable_reg = 0xB680 = 46720 => update Data_numblock, data_reg, data_numreg of node
+ update_enable_reg = 0xB640 = 46656 => update Offset temp, humidity, pressure, analog value
+ update_enable_reg = 0xB620 = 46624 => update Delta temp, humidity, pressure
+ update_enable_reg = 0xB610 = 46608 => update CT for WS433-AC
+ update_enable_reg = 0xB608 = 46600 => update Cut-off for WS433-AC
+ password = 190577
READ: cmd 03
WRITE: cmd 16

## Memmap of WS433-M12F and ATE
MODBUS MEMORY MAP FOR WIRELESS TEMPERATURE SENSOR WS433-M12F WITH ATE-xx
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 2 | 4 | Temperature value of sensor Node (parameter 1) | -40..+125oC |  | float | Read | Value from temperature sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | same value as parameter 1
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Offset value of parameter in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter 1 in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 2 | 4 | Delta_main |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40413 | 412 | 19C | 16 | 2 | 4 | Offset_main |  | 0 | float | Read/Write | Offset value to correct the value for parameter 1
| 40415 | 414 | 19E | 16 | 2 | 4 | Offset_second |  | 0 | float | Read/Write | Not Applicable, Offset value to correct the value for parameter 2
| 40417 | 416 | 1A0 | 16 | 6 | 12 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V3.x

## Memmap of WS433-M12F and ATH
MODBUS MEMORY MAP FOR WIRELESS TEMPERATURE SENSOR WS433-M12F WITH ATH-xx
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 2 | 4 | Humidity value of sensor Node (parameter 1) | 0..100% |  | float | Read | Value from humidity sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from humidity sensor. This value is parameter 2 of a wireless sensor node
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Offset value of parameter in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter 1 in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 2 | 4 | Delta_main |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40413 | 412 | 19C | 16 | 2 | 4 | Offset_main |  | 0 | float | Read/Write | Offset value to correct the value for parameter 1
| 40415 | 414 | 19E | 16 | 2 | 4 | Offset_second |  | 0 | float | Read/Write | Offset value to correct the value for parameter 2
| 40417 | 416 | 1A0 | 16 | 6 | 12 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V3.x

## Memmap of WS433-M12F and ADP
MODBUS MEMORY MAP FOR WIRELESS TEMPERATURE SENSOR WS433-M12F WITH ADP-xx
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 2 | 4 | Differential Pressure value of sensor Node (parameter 1) | -125..+125Pa |  | float | Read | Value from differential pressure sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from differential pressure sensor. This value is parameter 2 of a wireless sensor node
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Offset value of parameter in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter 1 in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 2 | 4 | Delta_main |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40413 | 412 | 19C | 16 | 2 | 4 | Offset_main |  | 0 | float | Read/Write | Offset value to correct the value for parameter 1
| 40415 | 414 | 19E | 16 | 2 | 4 | Offset_second |  | 0 | float | Read/Write | Offset value to correct the value for parameter 2
| 40417 | 416 | 1A0 | 16 | 6 | 12 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V3.x

## Memmap of WS433-M12F and PPS
MODBUS MEMORY MAP FOR WIRELESS TEMPERATURE SENSOR WS433-M12F WITH PPS-xx
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 2 | 4 | Pressure value of sensor Node (parameter 1) | 0..100% |  | float | Read | Value from pressure sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from pressure sensor. This value is parameter 2 of a wireless sensor node
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Offset value of parameter in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter 1 in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 2 | 4 | Delta_main |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40413 | 412 | 19C | 16 | 2 | 4 | Offset_main |  | 0 | float | Read/Write | Offset value to correct the value for parameter 1
| 40415 | 414 | 19E | 16 | 2 | 4 | Offset_second |  | 0 | float | Read/Write | Offset value to correct the value for parameter 2
| 40417 | 416 | 1A0 | 16 | 6 | 12 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V3.x

## Memmap of WS433-AC
MODBUS MEMORY MAP FOR WIRELESS AC CURRENT SENSOR WS433-AC
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 2 | 4 | AC Current value of sensor Node (parameter 1) | A |  | float | Read | Value from ac current sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | same value as parameter 1
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Offset value of parameter 1 in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter 1 in its Flash; + Write "update enable = 0xB610 = 46608" => to allow sensor Node to write the setting values of CT factor value of Current Transformer in its Flash; + Write "update enable = 0xB608 = 46600" => to allow sensor Node to write the setting values of CutOff current value of main parameter in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 2 | 4 | Delta_ac current |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40413 | 412 | 19C | 16 | 2 | 4 | Offset_ac current |  | 0 | float | Read/Write | Offset value to correct the value for parameter 1
| 40415 | 414 | 19E | 16 | 2 | 4 | Cutoff _ac current |  | 0.5 | float | Read/Write | Cut-off current value, this is the threshold to force ac current value = 0 when the load current is less then the threshold
| 40417 | 416 | 1A0 | 16 | 2 | 4 | CT_factory |  | 40 | float | Read/Write | CT factor value of Current Transformer
| 40419 | 418 | 1A2 | 16 | 4 | 8 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V3.x

## Memmap of WS433-DI and Status
MODBUS MEMORY MAP FOR WIRELESS DIGITAL INPUT SENSOR WS433-DI WITH LOGIC STATUS INPUT
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 1 | 2 | Logic status 1 of sensor Node (parameter 1) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value is parameter 1 of a wireless sensor node
| 30003 | 2 | 2 | 4 | 1 | 2 | Logic status 2 of sensor Node (parameter 2) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value is parameter 2 of a wireless sensor node
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | N/A |  |  |  | Read | Not Applicable
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Pulse width value of digital input in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Not Applicable. Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 1 | 2 | Delta_counter |  | 1 | uint16 | Read/Write | Not Applicable. Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40412 | 411 | 19B | 16 | 1 | 2 | Pulse width 1 | 1-10000(ms) | 10 | uint16 | Read/Write | Pulse width value for the digital input 1, this is the minimum threshold to allow digital input detect pulse
| 40413 | 412 | 19C | 16 | 1 | 2 | Pulse width 2 | 1-10000(ms) | 10 | uint16 | Read/Write | Pulse width value for the digital input 2, this is the minimum threshold to allow digital input detect pulse
| 40414 | 413 | 19D | 16 | 9 | 18 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V3.x

## Memmap of WS433-DI and Counter
MODBUS MEMORY MAP FOR WIRELESS DIGITAL INPUT SENSOR WS433-DI WITH COUNTER INPUT
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 2 | 4 | Counter value 1 of sensor Node (parameter 1) | 0-999,999,999 |  | uint32 | Read | Value from digital input sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | Counter value 2 of sensor Node (parameter 2) | 0-999,999,999 |  | uint32 | Read | Value from digital input sensor. This value is parameter 2 of a wireless sensor node
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Not Applicable. Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Not Applicable. Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Not Applicable. Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Not Applicable. Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Not Applicable. Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Not Applicable. Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Not Applicable. Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Not Applicable. Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Not Applicable. Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Pulse width value of digital input in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 1 | 2 | Delta_counter |  | 1 | uint16 | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40412 | 411 | 19B | 16 | 1 | 2 | Pulse width 1 | 1-10000(ms) | 10 | uint16 | Read/Write | Pulse width value for the digital input 1, this is the minimum threshold to allow digital input detect pulse
| 40413 | 412 | 19C | 16 | 1 | 2 | Pulse width 2 | 1-10000(ms) | 10 | uint16 | Read/Write | Pulse width value for the digital input 2, this is the minimum threshold to allow digital input detect pulse
| 40414 | 413 | 19D | 16 | 9 | 18 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V3.x

## Memmap of WS433-VL
MODBUS MEMORY MAP FOR WIRELESS 0..3VDC INPUT SENSOR WS433-VL
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 1 | 2 | Analog value 1 of sensor Node (parameter 1) | 0-3000 |  | uint16 | Read | Value from 0..3VDC input sensor. This value is parameter 1 of a wireless sensor node
| 30003 | 2 | 2 | 4 | 1 | 2 | Analog value 2 of sensor Node (parameter 2) | 0-3000 |  | uint16 | Read | Value from 0..3VDC input sensor. This value is parameter 2 of a wireless sensor node
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | N/A |  |  |  | Read | Not Applicable
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Offset value of parameter in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 1 | 2 | Delta_analog |  | 0 | uint16 | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40412 | 411 | 19B | 16 | 1 | 2 | Offset_analog 1 |  | 0 | uint16 | Read/Write | Offset value to correct the value for parameter 1
| 40413 | 412 | 19C | 16 | 1 | 2 | Offset_analog 2 |  | 0 | uint16 | Read/Write | Offset value to correct the value for parameter 2
| 40414 | 413 | 19D | 16 | 9 | 18 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V3.x

## Memmap of WS433-MA
MODBUS MEMORY MAP FOR WIRELESS 0..20MA INPUT SENSOR WS433-MA
Please enter Sensor Node's ID (1 .. 40): | [6 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 | 1 | 2 | Analog value 1 of sensor Node (parameter 1) | 0-3000 |  | uint16 | Read | Value from 0..20mA input sensor. This value is parameter 1 of a wireless sensor node
| 30003 | 2 | 2 | 4 | 1 | 2 | Value of parameter 2 of sensor Node | 0-3000 |  | uint16 | Read | same value as parameter 1
| 30004 | 3 | 3 | 4 | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type: + Hi-Byte = 0: No error + Hi-Byte = 1: Just exchange the sensor module but wireless module has not been reset ==> please take out the battery for 20s then install it again to reset wireless module to recognize the new sensor module + Hi-Byte = 2: error, sensor port M12F shorted to GND + Hi-Byte = 3: error, sensor port M12F shorted to Vcc + Hi-Byte = 4: error, sensor port M12F shorted each other + Hi-Byte = 51: check sum error of sensor port + Lo-Byte = 1: ambient temperature sensor + Lo-Byte = 2: ambient humidity sensor + Lo-Byte = 3: ambient differential pressure sensor + Lo-Byte = 4: process pressure sensor + Lo-Byte = 5: 1-channel AC 5A current sensor + Lo-Byte = 6: 2-channel digital input with counters + Lo-Byte = 7: 2-channel digital input with status detecting + Lo-Byte = 8: 2-channel 3VDC analog input + Lo-Byte = 9: 1-channel 0-20mA analog input + Lo-Byte = 10: 4-relay output, SPST contacts + Lo-Byte = 11: 2-relay output, SPDT contacts + Lo-Byte = 12: ambient light sensor + Lo-Byte = 255: NO sensor
| 30005 | 4 | 4 | 4 | 2 | 4 | N/A |  |  |  | Read | Not Applicable
| 30007 | 6 | 6 | 4 | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2: + If parameter 1's value > high threshold 1 => Hi-Byte of Logic status = 1 + If parameter 1's value < low threshold 1 => Hi-Byte of Logic status = 0 + If parameter 2's value > high threshold 2 => Lo-Byte of Logic status = 1 + If parameter 2's value < low threshold 2 => Lo-Byte of Logic status = 0 + If parameter 1 is digital => Hi-Byte of Logic status = parameter 1's value + If parameter 2 is digital => Lo-Byte of Logic status = parameter 2's value | for sensor with V3.x
| 30008 | 7 | 7 | 4 | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V3.x
| 30010 | 9 | 9 | 4 | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V3.x
| 30012 | 11 | B | 4 | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30014 | 13 | D | 4 | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
| 30016 | 15 | F | 4 | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V3.x
| 30018 | 17 | 11 | 4 | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V3.x
| 30020 | 19 | 13 | 4 | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V3.x
| 30022 | 21 | 15 | 4 | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V3.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning 99: Have not received data from wireless sensor 0: when data from wireless sensor just arrived in within "cmp time 1" seconds 1: when data from wireless sensor just arrived in within "cmp time 2" seconds 2: when data from wireless sensor just arrived in within "cmp time 3" seconds 3: when data from wireless sensor just arrived in within "cmp time 4" seconds 4: when data from wireless sensor just arrived in within "cmp time 5" seconds 5: when data from wireless sensor just arrived in within "cmp time 6" seconds 6: when data from wireless sensor just arrived in within "cmp time 7" seconds 7: when data from wireless sensor just arrived in within "cmp time 8" seconds 8: when data from wireless sensor just arrived in within "cmp time 9" seconds 9: when data from wireless sensor had arrived longer than "cmp time 9" seconds
| 40069 | 68 | 44 | 3 | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning RSSI = 0..-54dBm => RSSI Status = 4 (stronghest RF signal) RSSI = -55..-69dBm => RSSI Status = 3 RSSI = -70..-79dBm => RSSI Status = 2 RSSI = -80..-100dBm => RSSI Status = 1 RSSI < -100dBm => RSSI Status = 0
| 40189 | 188 | BC | 3 | 1 | 2 | Sync status of Node | 0-2, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only, see below its meaning If the Node ID is even ==> read the Lo-Byte only, see below its meaning To define the configuration of wireless sensor is successful or NOT? 0: sync ok, 1: sync start, 2: cfg error, 99: nothing to sync
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 16 | 1 | 2 | Update_enable |  | 0 | hex | Read/Write | + Write "update enable = 0xB601 = 46593" => to allow sensor Node to write the setting values of Cycle_wakeup and cycle_healthsta in its Flash; + Write "update enable = 0xB680 = 46720" => to allow sensor Node to write the setting values of Data_numblock, data_reg, and data_numreg in its Flash; + Write "update enable = 0xB640 = 46656" => to allow sensor Node to write the setting values of Offset value of parameter in its Flash; + Write "update enable = 0xB620 = 46624" => to allow sensor Node to write the setting values of Delta value of parameter in its Flash;
| 40402 | 401 | 191 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40403 | 402 | 192 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40404 | 403 | 193 | 16 | 1 | 2 | Data_numblock |  | 1 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40405 | 404 | 194 | 16 | 1 | 2 | Data_reg 1 |  | 8 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40406 | 405 | 195 | 16 | 1 | 2 | Data_numreg 1 |  | 23 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40407 | 406 | 196 | 16 | 1 | 2 | Data_reg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40408 | 407 | 197 | 16 | 1 | 2 | Data_numReg 2 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40409 | 408 | 198 | 16 | 1 | 2 | Data_reg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40410 | 409 | 199 | 16 | 1 | 2 | Data_numReg 3 |  | 0 | uint16 | Read/Write | Data frame definition, only for advanced users
| 40411 | 410 | 19A | 16 | 1 | 2 | Delta_analog |  | 0 | uint16 | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value is changed from the last value a delta value which is higher than the threshold.
| 40412 | 411 | 19B | 16 | 1 | 2 | Offset_analog 1 |  | 0 | uint16 | Read/Write | Offset value to correct the value for parameter 1
| 40413 | 412 | 19C | 16 | 1 | 2 | Offset_analog 2 |  | 0 | uint16 | Read/Write | Not Applicable. Offset value to correct the value for parameter 2
| 40414 | 413 | 19D | 16 | 9 | 18 | Spare |  |  |  | Read/Write | Not Applicable
| 40423 | 422 | 1A6 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V3.x
| 40425 | 424 | 1A8 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V3.x
| 40427 | 426 | 1AA | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V3.x
| 40429 | 428 | 1AC | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V3.x

## Sensor là AC 5A (hidden)
Modbus Register | # of register | Adr | Size | Description | Range | Default | Format | Property | Comment
41216 | 1 |  | 2 | %Battery Node1 | 10,30,60,99 |  | uint16 | Read | Wireless Sensor là loại cảm biến đo dòng AC, 0xA100..0xA120
41217 | 2 |  | 4 | Current Node1 | % |  | float | Read | Current output (A)
41219 | 1 |  | 2 | Status Node1 | 0-255 |  | uint16 | Read | Byte Hi "error", byte lo "loại sensor": + byte lo = 1: cảm biến nhiệt độ + byte lo = 2: cảm biến độ ẩm + byte lo = 3: cảm biến chênh áp môi trường + byte lo = 4: cảm biến áp suất + byte lo = 5: cảm biến 1 kênh đo dòng AC + byte lo = 6: cảm biến digital input, 2 kênh Counter + byte lo = 7: cảm biến digital input, 2 kênh Status + byte lo = 8: cảm biến 2 kênh volts 3vdc + byte lo = 9: cảm biến 1 kênh 0-20mA + byte lo = 10: cảm biến ngõ ra 4 kênh relay SPST + byte lo = 11: cảm biến ngõ ra 2 kênh relay SPDT + byte lo = 12: cảm biến ánh sáng môi trường + byte lo = 255: không có cảm biến + byte hi = 0: không có lỗi + byte hi = 1: đã thay đổi loại sensor port M12F mà chưa reset để nhận dạng cảm biến mới + byte hi = 2: sensor port M12F chạm GND + byte hi = 3: sensor port M12F chạm Vcc + byte hi = 4: sensor port M12F chạm nhau + byte hi = 51: sensor port uart bị lỗi check sum
41220 | 2 |  | 4 | Temperature Node1 | oC |  | float | Read
41472 | 1 |  | 2 | %Battery Node2 | 10,30,60,99 |  | uint16 | Read | 0xA200..0xA220
41473 | 2 |  | 4 | Current Node2 | % |  | float | Read
41475 | 1 |  | 2 | Status Node2 | 0-255 |  | uint16 | Read
41476 | 2 |  | 4 | Temperature Node2 | oC |  | float | Read
41728 | 1 |  | 2 | %Battery Node3 | 10,30,60,99 |  | uint16 | Read | 0xA300..0xA320
41729 | 2 |  | 4 | Current Node3 | % |  | float | Read
41731 | 1 |  | 2 | Status Node3 | 0-255 |  | uint16 | Read
41732 | 2 |  | 4 | Temperature Node3 | oC |  | float | Read
41984 | 1 |  | 2 | %Battery Node4 | 10,30,60,99 |  | uint16 | Read | 0xA400..0xA420
41985 | 2 |  | 4 | Current Node4 | % |  | float | Read
41987 | 1 |  | 2 | Status Node4 | 0-255 |  | uint16 | Read
41988 | 2 |  | 4 | Temperature Node4 | oC |  | float | Read
42240 | 1 |  | 2 | %Battery Node5 | 10,30,60,99 |  | uint16 | Read | 0xA500..0xA520
42241 | 2 |  | 4 | Current Node5 | % |  | float | Read
42243 | 1 |  | 2 | Status Node5 | 0-255 |  | uint16 | Read
42244 | 2 |  | 4 | Temperature Node5 | oC |  | float | Read
42496 | 1 |  | 2 | %Battery Node6 | 10,30,60,99 |  | uint16 | Read | 0xA600..0xA620
42497 | 2 |  | 4 | Current Node6 | % |  | float | Read
42499 | 1 |  | 2 | Status Node6 | 0-255 |  | uint16 | Read
42500 | 2 |  | 4 | Temperature Node6 | oC |  | float | Read
42752 | 1 |  | 2 | %Battery Node7 | 10,30,60,99 |  | uint16 | Read | 0xA700..0xA720
42753 | 2 |  | 4 | Current Node7 | % |  | float | Read
42755 | 1 |  | 2 | Status Node7 | 0-255 |  | uint16 | Read
42756 | 2 |  | 4 | Temperature Node7 | oC |  | float | Read
43008 | 1 |  | 2 | %Battery Node8 | 10,30,60,99 |  | uint16 | Read | 0xA800..0xA820
43009 | 2 |  | 4 | Current Node8 | % |  | float | Read
43011 | 1 |  | 2 | Status Node8 | 0-255 |  | uint16 | Read
43012 | 2 |  | 4 | Temperature Node8 | oC |  | float | Read
43264 | 1 |  | 2 | %Battery Node9 | 10,30,60,99 |  | uint16 | Read | 0xA900..0xA920
43265 | 2 |  | 4 | Current Node9 | % |  | float | Read
43267 | 1 |  | 2 | Status Node9 | 0-255 |  | uint16 | Read
43268 | 2 |  | 4 | Temperature Node9 | oC |  | float | Read
43520 | 1 |  | 2 | %Battery Node10 | 10,30,60,99 |  | uint16 | Read | 0xAA00..0xAA20
43521 | 2 |  | 4 | Current Node10 | % |  | float | Read
43523 | 1 |  | 2 | Status Node10 | 0-255 |  | uint16 | Read
43524 | 2 |  | 4 | Temperature Node10 | oC |  | float | Read
45312 | 1 |  | 2 | %Battery Node11 | 10,30,60,99 |  | uint16 | Read | 0xB100..0xB120
45313 | 2 |  | 4 | Current Node11 | % |  | float | Read
45315 | 1 |  | 2 | Status Node11 | 0-255 |  | uint16 | Read
45316 | 2 |  | 4 | Temperature Node11 | oC |  | float | Read
45568 | 1 |  | 2 | %Battery Node12 | 10,30,60,99 |  | uint16 | Read | 0xB200..0xB220
45569 | 2 |  | 4 | Current Node12 | % |  | float | Read
45571 | 1 |  | 2 | Status Node12 | 0-255 |  | uint16 | Read
45572 | 2 |  | 4 | Temperature Node12 | oC |  | float | Read
45824 | 1 |  | 2 | %Battery Node13 | 10,30,60,99 |  | uint16 | Read | 0xB300..0xB320
45825 | 2 |  | 4 | Current Node13 | % |  | float | Read
45827 | 1 |  | 2 | Status Node13 | 0-255 |  | uint16 | Read
45828 | 2 |  | 4 | Temperature Node13 | oC |  | float | Read
46080 | 1 |  | 2 | %Battery Node14 | 10,30,60,99 |  | uint16 | Read | 0xB400..0xB420
46081 | 2 |  | 4 | Current Node14 | % |  | float | Read
46083 | 1 |  | 2 | Status Node14 | 0-255 |  | uint16 | Read
46084 | 2 |  | 4 | Temperature Node14 | oC |  | float | Read
46336 | 1 |  | 2 | %Battery Node15 | 10,30,60,99 |  | uint16 | Read | 0xB500..0xB520
46337 | 2 |  | 4 | Current Node15 | % |  | float | Read
46339 | 1 |  | 2 | Status Node15 | 0-255 |  | uint16 | Read
46340 | 2 |  | 4 | Temperature Node15 | oC |  | float | Read
46592 | 1 |  | 2 | %Battery Node16 | 10,30,60,99 |  | uint16 | Read | 0xB600..0xB620
46593 | 2 |  | 4 | Current Node16 | % |  | float | Read
46595 | 1 |  | 2 | Status Node16 | 0-255 |  | uint16 | Read
46596 | 2 |  | 4 | Temperature Node16 | oC |  | float | Read
46848 | 1 |  | 2 | %Battery Node17 | 10,30,60,99 |  | uint16 | Read | 0xB700..0xB720
46849 | 2 |  | 4 | Current Node17 | % |  | float | Read
46851 | 1 |  | 2 | Status Node17 | 0-255 |  | uint16 | Read
46852 | 2 |  | 4 | Temperature Node17 | oC |  | float | Read
47104 | 1 |  | 2 | %Battery Node18 | 10,30,60,99 |  | uint16 | Read | 0xB800..0xB820
47105 | 2 |  | 4 | Current Node18 | % |  | float | Read
47107 | 1 |  | 2 | Status Node18 | 0-255 |  | uint16 | Read
47108 | 2 |  | 4 | Temperature Node18 | oC |  | float | Read
47360 | 1 |  | 2 | %Battery Node19 | 10,30,60,99 |  | uint16 | Read | 0xB900..0xB920
47361 | 2 |  | 4 | Current Node19 | % |  | float | Read
47363 | 1 |  | 2 | Status Node19 | 0-255 |  | uint16 | Read
47364 | 2 |  | 4 | Temperature Node19 | oC |  | float | Read
47616 | 1 |  | 2 | %Battery Node20 | 10,30,60,99 |  | uint16 | Read | 0xBA00..0xBA20
47617 | 2 |  | 4 | Current Node20 | % |  | float | Read
47619 | 1 |  | 2 | Status Node20 | 0-255 |  | uint16 | Read
47620 | 2 |  | 4 | Temperature Node20 | oC |  | float | Read
49408 | 1 |  | 2 | %Battery Node21 | 10,30,60,99 |  | uint16 | Read | 0xC100..0xC120
49409 | 2 |  | 4 | Current Node21 | % |  | float | Read
49411 | 1 |  | 2 | Status Node21 | 0-255 |  | uint16 | Read
49412 | 2 |  | 4 | Temperature Node21 | oC |  | float | Read
49664 | 1 |  | 2 | %Battery Node22 | 10,30,60,99 |  | uint16 | Read | 0xC200..0xC220
49665 | 2 |  | 4 | Current Node22 | % |  | float | Read
49667 | 1 |  | 2 | Status Node22 | 0-255 |  | uint16 | Read
49668 | 2 |  | 4 | Temperature Node22 | oC |  | float | Read
49920 | 1 |  | 2 | %Battery Node23 | 10,30,60,99 |  | uint16 | Read | 0xC300..0xC320
49921 | 2 |  | 4 | Current Node23 | % |  | float | Read
49923 | 1 |  | 2 | Status Node23 | 0-255 |  | uint16 | Read
49924 | 2 |  | 4 | Temperature Node23 | oC |  | float | Read
50176 | 1 |  | 2 | %Battery Node24 | 10,30,60,99 |  | uint16 | Read | 0xC400..0xC420
50177 | 2 |  | 4 | Current Node24 | % |  | float | Read
50179 | 1 |  | 2 | Status Node24 | 0-255 |  | uint16 | Read
50180 | 2 |  | 4 | Temperature Node24 | oC |  | float | Read
50432 | 1 |  | 2 | %Battery Node25 | 10,30,60,99 |  | uint16 | Read | 0xC500..0xC520
50433 | 2 |  | 4 | Current Node25 | % |  | float | Read
50435 | 1 |  | 2 | Status Node25 | 0-255 |  | uint16 | Read
50436 | 2 |  | 4 | Temperature Node25 | oC |  | float | Read
50688 | 1 |  | 2 | %Battery Node26 | 10,30,60,99 |  | uint16 | Read | 0xC600..0xC620
50689 | 2 |  | 4 | Current Node26 | % |  | float | Read
50691 | 1 |  | 2 | Status Node26 | 0-255 |  | uint16 | Read
50692 | 2 |  | 4 | Temperature Node26 | oC |  | float | Read
50944 | 1 |  | 2 | %Battery Node27 | 10,30,60,99 |  | uint16 | Read | 0xC700..0xC720
50945 | 2 |  | 4 | Current Node27 | % |  | float | Read
50947 | 1 |  | 2 | Status Node27 | 0-255 |  | uint16 | Read
50948 | 2 |  | 4 | Temperature Node27 | oC |  | float | Read
51200 | 1 |  | 2 | %Battery Node28 | 10,30,60,99 |  | uint16 | Read | 0xC800..0xC820
51201 | 2 |  | 4 | Current Node28 | % |  | float | Read
51203 | 1 |  | 2 | Status Node28 | 0-255 |  | uint16 | Read
51204 | 2 |  | 4 | Temperature Node28 | oC |  | float | Read
51456 | 1 |  | 2 | %Battery Node29 | 10,30,60,99 |  | uint16 | Read | 0xC900..0xC920
51457 | 2 |  | 4 | Current Node29 | % |  | float | Read
51459 | 1 |  | 2 | Status Node29 | 0-255 |  | uint16 | Read
51460 | 2 |  | 4 | Temperature Node29 | oC |  | float | Read
51712 | 1 |  | 2 | %Battery Node30 | 10,30,60,99 |  | uint16 | Read | 0xCA00..0xCA20
51713 | 2 |  | 4 | Current Node30 | % |  | float | Read
51715 | 1 |  | 2 | Status Node30 | 0-255 |  | uint16 | Read
51716 | 2 |  | 4 | Temperature Node30 | oC |  | float | Read
53504 | 1 |  | 2 | %Battery Node31 | 10,30,60,99 |  | uint16 | Read | 0xD100..0xD120
53505 | 2 |  | 4 | Current Node31 | % |  | float | Read
53507 | 1 |  | 2 | Status Node31 | 0-255 |  | uint16 | Read
53508 | 2 |  | 4 | Temperature Node31 | oC |  | float | Read
53760 | 1 |  | 2 | %Battery Node32 | 10,30,60,99 |  | uint16 | Read | 0xD200..0xD220
53761 | 2 |  | 4 | Current Node32 | % |  | float | Read
53763 | 1 |  | 2 | Status Node32 | 0-255 |  | uint16 | Read
53764 | 2 |  | 4 | Temperature Node32 | oC |  | float | Read
54016 | 1 |  | 2 | %Battery Node33 | 10,30,60,99 |  | uint16 | Read | 0xD300..0xD320
54017 | 2 |  | 4 | Current Node33 | % |  | float | Read
54019 | 1 |  | 2 | Status Node33 | 0-255 |  | uint16 | Read
54020 | 2 |  | 4 | Temperature Node33 | oC |  | float | Read
54272 | 1 |  | 2 | %Battery Node34 | 10,30,60,99 |  | uint16 | Read | 0xD400..0xD420
54273 | 2 |  | 4 | Current Node34 | % |  | float | Read
54275 | 1 |  | 2 | Status Node34 | 0-255 |  | uint16 | Read
54276 | 2 |  | 4 | Temperature Node34 | oC |  | float | Read
54528 | 1 |  | 2 | %Battery Node35 | 10,30,60,99 |  | uint16 | Read | 0xD500..0xD520
54529 | 2 |  | 4 | Current Node35 | % |  | float | Read
54531 | 1 |  | 2 | Status Node35 | 0-255 |  | uint16 | Read
54532 | 2 |  | 4 | Temperature Node35 | oC |  | float | Read
54784 | 1 |  | 2 | %Battery Node36 | 10,30,60,99 |  | uint16 | Read | 0xD600..0xD620
54785 | 2 |  | 4 | Current Node36 | % |  | float | Read
54787 | 1 |  | 2 | Status Node36 | 0-255 |  | uint16 | Read
54788 | 2 |  | 4 | Temperature Node36 | oC |  | float | Read
55040 | 1 |  | 2 | %Battery Node37 | 10,30,60,99 |  | uint16 | Read | 0xD700..0xD720
55041 | 2 |  | 4 | Current Node37 | % |  | float | Read
55043 | 1 |  | 2 | Status Node37 | 0-255 |  | uint16 | Read
55044 | 2 |  | 4 | Temperature Node37 | oC |  | float | Read
55296 | 1 |  | 2 | %Battery Node38 | 10,30,60,99 |  | uint16 | Read | 0xD800..0xD820
55297 | 2 |  | 4 | Current Node38 | % |  | float | Read
55299 | 1 |  | 2 | Status Node38 | 0-255 |  | uint16 | Read
55300 | 2 |  | 4 | Temperature Node38 | oC |  | float | Read
55552 | 1 |  | 2 | %Battery Node39 | 10,30,60,99 |  | uint16 | Read | 0xD900..0xD920
55553 | 2 |  | 4 | Current Node39 | % |  | float | Read
55555 | 1 |  | 2 | Status Node39 | 0-255 |  | uint16 | Read
55556 | 2 |  | 4 | Temperature Node39 | oC |  | float | Read
55808 | 1 |  | 2 | %Battery Node40 | 10,30,60,99 |  | uint16 | Read | 0xDA00..0xDA20
55809 | 2 |  | 4 | Current Node40 | % |  | float | Read
55811 | 1 |  | 2 | Status Node40 | 0-255 |  | uint16 | Read
55812 | 2 |  | 4 | Temperature Node40 | oC |  | float | Read
256 | 1 | 0 | 2 | modbus address | 1-247 | 1 | uint16 | Read/Write
257 | 1 | 2 | 2 | modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
258 | 1 | 4 | 2 | modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
259 | 9 | 6 | 18 | serial number |  |  | string | Read/Write(PW)
268 | 2 | 24 | 4 | password for setting |  |  | uint32 | Read/Write | Password = 190577
270 | 2 | 28 | 4 | receiver id |  |  | uint32 | Read/Write(PW)
272 | 1 | 32 | 2 | num of node | 0-40 |  | uint16 | Read/Write
273 | 2 | 34 | 4 | node id 1 |  |  | uint32 | Read/Write
275 | 2 | 38 | 4 | node id 2 |  |  | uint32 | Read/Write
277 | 2 | 42 | 4 | node id 3 |  |  | uint32 | Read/Write
279 | 2 | 46 | 4 | node id 4 |  |  | uint32 | Read/Write
281 | 2 | 50 | 4 | node id 5 |  |  | uint32 | Read/Write
283 | 2 | 54 | 4 | node id 6 |  |  | uint32 | Read/Write
285 | 2 | 58 | 4 | node id 7 |  |  | uint32 | Read/Write
287 | 2 | 62 | 4 | node id 8 |  |  | uint32 | Read/Write
289 | 2 | 66 | 4 | node id 9 |  |  | uint32 | Read/Write
291 | 2 | 70 | 4 | node id 10 |  |  | uint32 | Read/Write
293 | 2 | 74 | 4 | node id 11 |  |  | uint32 | Read/Write
295 | 2 | 78 | 4 | node id 12 |  |  | uint32 | Read/Write
297 | 2 | 82 | 4 | node id 13 |  |  | uint32 | Read/Write
299 | 2 | 86 | 4 | node id 14 |  |  | uint32 | Read/Write
301 | 2 | 90 | 4 | node id 15 |  |  | uint32 | Read/Write
303 | 2 | 94 | 4 | node id 16 |  |  | uint32 | Read/Write
305 | 2 | 98 | 4 | node id 17 |  |  | uint32 | Read/Write
307 | 2 | 102 | 4 | node id 18 |  |  | uint32 | Read/Write
309 | 2 | 106 | 4 | node id 19 |  |  | uint32 | Read/Write
311 | 2 | 110 | 4 | node id 20 |  |  | uint32 | Read/Write
313 | 2 | 114 | 4 | node id 21 |  |  | uint32 | Read/Write
315 | 2 | 118 | 4 | node id 22 |  |  | uint32 | Read/Write
317 | 2 | 122 | 4 | node id 23 |  |  | uint32 | Read/Write
319 | 2 | 126 | 4 | node id 24 |  |  | uint32 | Read/Write
321 | 2 | 130 | 4 | node id 25 |  |  | uint32 | Read/Write
323 | 2 | 134 | 4 | node id 26 |  |  | uint32 | Read/Write
325 | 2 | 138 | 4 | node id 27 |  |  | uint32 | Read/Write
327 | 2 | 142 | 4 | node id 28 |  |  | uint32 | Read/Write
329 | 2 | 146 | 4 | node id 29 |  |  | uint32 | Read/Write
331 | 2 | 150 | 4 | node id 30 |  |  | uint32 | Read/Write
333 | 2 | 154 | 4 | node id 31 |  |  | uint32 | Read/Write
335 | 2 | 158 | 4 | node id 32 |  |  | uint32 | Read/Write
337 | 2 | 162 | 4 | node id 33 |  |  | uint32 | Read/Write
339 | 2 | 166 | 4 | node id 34 |  |  | uint32 | Read/Write
341 | 2 | 170 | 4 | node id 35 |  |  | uint32 | Read/Write
343 | 2 | 174 | 4 | node id 36 |  |  | uint32 | Read/Write
345 | 2 | 178 | 4 | node id 37 |  |  | uint32 | Read/Write
347 | 2 | 182 | 4 | node id 38 |  |  | uint32 | Read/Write
349 | 2 | 186 | 4 | node id 39 |  |  | uint32 | Read/Write
351 | 2 | 190 | 4 | node id 40 |  |  | uint32 | Read/Write
353 | 1 | 194 | 2 | cmp time 1 |  | 15 | uint16 | Read/Write | second
354 | 1 | 196 | 2 | cmp time 2 |  | 30 | uint16 | Read/Write | second
355 | 1 | 198 | 2 | cmp time 3 |  | 45 | uint16 | Read/Write | second
356 | 1 | 200 | 2 | cmp time 4 |  | 60 | uint16 | Read/Write | second
357 | 1 | 202 | 2 | cmp time 5 |  | 300 | uint16 | Read/Write | second
358 | 1 | 204 | 2 | cmp time 6 |  | 600 | uint16 | Read/Write | second
359 | 1 | 206 | 2 | cmp time 7 |  | 900 | uint16 | Read/Write | second
360 | 1 | 208 | 2 | cmp time 8 |  | 1800 | uint16 | Read/Write | second
361 | 1 | 210 | 2 | cmp time 9 |  | 3600 | uint16 | Read/Write | second
362 | 37 | 212 | 74 | spare
399 | 1 | 286 | 2 | sync all node | 0-1 |  | uint16 | Read/Write | 1: restart sync
400 | 1 | 288 | 2 | Update_enable_Node1 |  |  | hex | Read/Write | + update enable = 0xB601 = 46593 => update Cycle_wakeup, cycle_healthstatus of node + update enable = 0xB680 = 46720 => update Data_numblock, data_reg, data_numreg of node + update enable = 0xB640 = 46656 => update Offset temp, humidity, pulse width 4 channel of node + update enable = 0xB620 = 46624 => update Delta temp, humidity, counter of node
401 | 1 | 290 | 2 | Cycle_wakeup_Node1 |  |  | uint16 | Read/Write
402 | 1 | 292 | 2 | Cycle_heathsta_Node1 |  |  | uint16 | Read/Write
403 | 1 | 294 | 2 | Data_numblock_Node1 |  |  | uint16 | Read/Write
404 | 1 | 296 | 2 | Data_reg 1_Node1 |  |  | uint16 | Read/Write
405 | 1 | 298 | 2 | Data_numreg 1_Node1 |  |  | uint16 | Read/Write
406 | 1 | 300 | 2 | Data_reg 2_Node1 |  |  | uint16 | Read/Write
407 | 1 | 302 | 2 | Data_numReg 2_Node1 |  |  | uint16 | Read/Write
408 | 1 | 304 | 2 | Data_reg 3_Node1 |  |  | uint16 | Read/Write
409 | 1 | 306 | 2 | Data_numReg 3_Node1 |  |  | uint16 | Read/Write
410 | 2 | 308 | 4 | Delta_Current_Node1 |  |  | float | Read/Write
412 | 2 | 312 | 4 | Offset_Current_Node1 |  |  | float | Read/Write
414 | 2 | 316 | 4 | CutOff_Node1 |  |  | float | Read/Write
416 | 2 | 320 | 4 | CT_Node1 |  |  | float | Read/Write
418 | 12 | 324 | 24 | Reserve_regs_Node1 |  |  |  | Read/Write
430 | 1 | 348 | 2 | Update_enable_Node2 |  |  | hex | Read/Write
431 | 1 | 350 | 2 | Cycle_wakeup_Node2 |  |  | uint16 | Read/Write
432 | 1 | 352 | 2 | Cycle_heathsta_Node2 |  |  | uint16 | Read/Write
433 | 1 | 354 | 2 | Data_numblock_Node2 |  |  | uint16 | Read/Write
434 | 1 | 356 | 2 | Data_reg 1_Node2 |  |  | uint16 | Read/Write
435 | 1 | 358 | 2 | Data_numreg 1_Node2 |  |  | uint16 | Read/Write
436 | 1 | 360 | 2 | Data_reg 2_Node2 |  |  | uint16 | Read/Write
437 | 1 | 362 | 2 | Data_numReg 2_Node2 |  |  | uint16 | Read/Write
438 | 1 | 364 | 2 | Data_reg 3_Node2 |  |  | uint16 | Read/Write
439 | 1 | 366 | 2 | Data_numReg 3_Node2 |  |  | uint16 | Read/Write
440 | 2 | 368 | 4 | Delta_Current_Node2 |  |  | float | Read/Write
442 | 2 | 372 | 4 | Offset_Current_Node2 |  |  | float | Read/Write
444 | 2 | 376 | 4 | CutOff_Node2 |  |  | float | Read/Write
446 | 2 | 380 | 4 | CT_Node2 |  |  | float | Read/Write
448 | 12 | 384 | 24 | Reserve_regs_Node2 |  |  |  | Read/Write
460 | 1 | 408 | 2 | Update_enable_Node3 |  |  | hex | Read/Write
461 | 1 | 410 | 2 | Cycle_wakeup_Node3 |  |  | uint16 | Read/Write
462 | 1 | 412 | 2 | Cycle_heathsta_Node3 |  |  | uint16 | Read/Write
463 | 1 | 414 | 2 | Data_numblock_Node3 |  |  | uint16 | Read/Write
464 | 1 | 416 | 2 | Data_reg 1_Node3 |  |  | uint16 | Read/Write
465 | 1 | 418 | 2 | Data_numreg 1_Node3 |  |  | uint16 | Read/Write
466 | 1 | 420 | 2 | Data_reg 2_Node3 |  |  | uint16 | Read/Write
467 | 1 | 422 | 2 | Data_numReg 2_Node3 |  |  | uint16 | Read/Write
468 | 1 | 424 | 2 | Data_reg 3_Node3 |  |  | uint16 | Read/Write
469 | 1 | 426 | 2 | Data_numReg 3_Node3 |  |  | uint16 | Read/Write
470 | 2 | 428 | 4 | Delta_Current_Node3 |  |  | float | Read/Write
472 | 2 | 432 | 4 | Offset_Current_Node3 |  |  | float | Read/Write
474 | 2 | 436 | 4 | CutOff_Node3 |  |  | float | Read/Write
476 | 2 | 440 | 4 | CT_Node3 |  |  | float | Read/Write
478 | 12 | 444 | 24 | Reserve_regs_Node3 |  |  |  | Read/Write
490 | 1 | 468 | 2 | Update_enable_Node4 |  |  | hex | Read/Write
491 | 1 | 470 | 2 | Cycle_wakeup_Node4 |  |  | uint16 | Read/Write
492 | 1 | 472 | 2 | Cycle_heathsta_Node4 |  |  | uint16 | Read/Write
493 | 1 | 474 | 2 | Data_numblock_Node4 |  |  | uint16 | Read/Write
494 | 1 | 476 | 2 | Data_reg 1_Node4 |  |  | uint16 | Read/Write
495 | 1 | 478 | 2 | Data_numreg 1_Node4 |  |  | uint16 | Read/Write
496 | 1 | 480 | 2 | Data_reg 2_Node4 |  |  | uint16 | Read/Write
497 | 1 | 482 | 2 | Data_numReg 2_Node4 |  |  | uint16 | Read/Write
498 | 1 | 484 | 2 | Data_reg 3_Node4 |  |  | uint16 | Read/Write
499 | 1 | 486 | 2 | Data_numReg 3_Node4 |  |  | uint16 | Read/Write
500 | 2 | 488 | 4 | Delta_Current_Node4 |  |  | float | Read/Write
502 | 2 | 492 | 4 | Offset_Current_Node4 |  |  | float | Read/Write
504 | 2 | 496 | 4 | CutOff_Node4 |  |  | float | Read/Write
506 | 2 | 500 | 4 | CT_Node4 |  |  | float | Read/Write
508 | 12 | 504 | 24 | Reserve_regs_Node4 |  |  |  | Read/Write
520 | 1 | 528 | 2 | Update_enable_Node5 |  |  | hex | Read/Write
521 | 1 | 530 | 2 | Cycle_wakeup_Node5 |  |  | uint16 | Read/Write
522 | 1 | 532 | 2 | Cycle_heathsta_Node5 |  |  | uint16 | Read/Write
523 | 1 | 534 | 2 | Data_numblock_Node5 |  |  | uint16 | Read/Write
524 | 1 | 536 | 2 | Data_reg 1_Node5 |  |  | uint16 | Read/Write
525 | 1 | 538 | 2 | Data_numreg 1_Node5 |  |  | uint16 | Read/Write
526 | 1 | 540 | 2 | Data_reg 2_Node5 |  |  | uint16 | Read/Write
527 | 1 | 542 | 2 | Data_numReg 2_Node5 |  |  | uint16 | Read/Write
528 | 1 | 544 | 2 | Data_reg 3_Node5 |  |  | uint16 | Read/Write
529 | 1 | 546 | 2 | Data_numReg 3_Node5 |  |  | uint16 | Read/Write
530 | 2 | 548 | 4 | Delta_Current_Node5 |  |  | float | Read/Write
532 | 2 | 552 | 4 | Offset_Current_Node5 |  |  | float | Read/Write
534 | 2 | 556 | 4 | CutOff_Node5 |  |  | float | Read/Write
536 | 2 | 560 | 4 | CT_Node5 |  |  | float | Read/Write
538 | 12 | 564 | 24 | Reserve_regs_Node5 |  |  |  | Read/Write
550 | 1 | 588 | 2 | Update_enable_Node6 |  |  | hex | Read/Write
551 | 1 | 590 | 2 | Cycle_wakeup_Node6 |  |  | uint16 | Read/Write
552 | 1 | 592 | 2 | Cycle_heathsta_Node6 |  |  | uint16 | Read/Write
553 | 1 | 594 | 2 | Data_numblock_Node6 |  |  | uint16 | Read/Write
554 | 1 | 596 | 2 | Data_reg 1_Node6 |  |  | uint16 | Read/Write
555 | 1 | 598 | 2 | Data_numreg 1_Node6 |  |  | uint16 | Read/Write
556 | 1 | 600 | 2 | Data_reg 2_Node6 |  |  | uint16 | Read/Write
557 | 1 | 602 | 2 | Data_numReg 2_Node6 |  |  | uint16 | Read/Write
558 | 1 | 604 | 2 | Data_reg 3_Node6 |  |  | uint16 | Read/Write
559 | 1 | 606 | 2 | Data_numReg 3_Node6 |  |  | uint16 | Read/Write
560 | 2 | 608 | 4 | Delta_Current_Node6 |  |  | float | Read/Write
562 | 2 | 612 | 4 | Offset_Current_Node6 |  |  | float | Read/Write
564 | 2 | 616 | 4 | CutOff_Node6 |  |  | float | Read/Write
566 | 2 | 620 | 4 | CT_Node6 |  |  | float | Read/Write
568 | 12 | 624 | 24 | Reserve_regs_Node6 |  |  |  | Read/Write
580 | 1 | 648 | 2 | Update_enable_Node7 |  |  | hex | Read/Write
581 | 1 | 650 | 2 | Cycle_wakeup_Node7 |  |  | uint16 | Read/Write
582 | 1 | 652 | 2 | Cycle_heathsta_Node7 |  |  | uint16 | Read/Write
583 | 1 | 654 | 2 | Data_numblock_Node7 |  |  | uint16 | Read/Write
584 | 1 | 656 | 2 | Data_reg 1_Node7 |  |  | uint16 | Read/Write
585 | 1 | 658 | 2 | Data_numreg 1_Node7 |  |  | uint16 | Read/Write
586 | 1 | 660 | 2 | Data_reg 2_Node7 |  |  | uint16 | Read/Write
587 | 1 | 662 | 2 | Data_numReg 2_Node7 |  |  | uint16 | Read/Write
588 | 1 | 664 | 2 | Data_reg 3_Node7 |  |  | uint16 | Read/Write
589 | 1 | 666 | 2 | Data_numReg 3_Node7 |  |  | uint16 | Read/Write
590 | 2 | 668 | 4 | Delta_Current_Node7 |  |  | float | Read/Write
592 | 2 | 672 | 4 | Offset_Current_Node7 |  |  | float | Read/Write
594 | 2 | 676 | 4 | CutOff_Node7 |  |  | float | Read/Write
596 | 2 | 680 | 4 | CT_Node7 |  |  | float | Read/Write
598 | 12 | 684 | 24 | Reserve_regs_Node7 |  |  |  | Read/Write
610 | 1 | 708 | 2 | Update_enable_Node8 |  |  | hex | Read/Write
611 | 1 | 710 | 2 | Cycle_wakeup_Node8 |  |  | uint16 | Read/Write
612 | 1 | 712 | 2 | Cycle_heathsta_Node8 |  |  | uint16 | Read/Write
613 | 1 | 714 | 2 | Data_numblock_Node8 |  |  | uint16 | Read/Write
614 | 1 | 716 | 2 | Data_reg 1_Node8 |  |  | uint16 | Read/Write
615 | 1 | 718 | 2 | Data_numreg 1_Node8 |  |  | uint16 | Read/Write
616 | 1 | 720 | 2 | Data_reg 2_Node8 |  |  | uint16 | Read/Write
617 | 1 | 722 | 2 | Data_numReg 2_Node8 |  |  | uint16 | Read/Write
618 | 1 | 724 | 2 | Data_reg 3_Node8 |  |  | uint16 | Read/Write
619 | 1 | 726 | 2 | Data_numReg 3_Node8 |  |  | uint16 | Read/Write
620 | 2 | 728 | 4 | Delta_Current_Node8 |  |  | float | Read/Write
622 | 2 | 732 | 4 | Offset_Current_Node8 |  |  | float | Read/Write
624 | 2 | 736 | 4 | CutOff_Node8 |  |  | float | Read/Write
626 | 2 | 740 | 4 | CT_Node8 |  |  | float | Read/Write
628 | 12 | 744 | 24 | Reserve_regs_Node8 |  |  |  | Read/Write
640 | 1 | 768 | 2 | Update_enable_Node9 |  |  | hex | Read/Write
641 | 1 | 770 | 2 | Cycle_wakeup_Node9 |  |  | uint16 | Read/Write
642 | 1 | 772 | 2 | Cycle_heathsta_Node9 |  |  | uint16 | Read/Write
643 | 1 | 774 | 2 | Data_numblock_Node9 |  |  | uint16 | Read/Write
644 | 1 | 776 | 2 | Data_reg 1_Node9 |  |  | uint16 | Read/Write
645 | 1 | 778 | 2 | Data_numreg 1_Node9 |  |  | uint16 | Read/Write
646 | 1 | 780 | 2 | Data_reg 2_Node9 |  |  | uint16 | Read/Write
647 | 1 | 782 | 2 | Data_numReg 2_Node9 |  |  | uint16 | Read/Write
648 | 1 | 784 | 2 | Data_reg 3_Node9 |  |  | uint16 | Read/Write
649 | 1 | 786 | 2 | Data_numReg 3_Node9 |  |  | uint16 | Read/Write
650 | 2 | 788 | 4 | Delta_Current_Node9 |  |  | float | Read/Write
652 | 2 | 792 | 4 | Offset_Current_Node9 |  |  | float | Read/Write
654 | 2 | 796 | 4 | CutOff_Node9 |  |  | float | Read/Write
656 | 2 | 800 | 4 | CT_Node9 |  |  | float | Read/Write
658 | 12 | 804 | 24 | Reserve_regs_Node9 |  |  |  | Read/Write
670 | 1 | 828 | 2 | Update_enable_Node10 |  |  | hex | Read/Write
671 | 1 | 830 | 2 | Cycle_wakeup_Node10 |  |  | uint16 | Read/Write
672 | 1 | 832 | 2 | Cycle_heathsta_Node10 |  |  | uint16 | Read/Write
673 | 1 | 834 | 2 | Data_numblock_Node10 |  |  | uint16 | Read/Write
674 | 1 | 836 | 2 | Data_reg 1_Node10 |  |  | uint16 | Read/Write
675 | 1 | 838 | 2 | Data_numreg 1_Node10 |  |  | uint16 | Read/Write
676 | 1 | 840 | 2 | Data_reg 2_Node10 |  |  | uint16 | Read/Write
677 | 1 | 842 | 2 | Data_numReg 2_Node10 |  |  | uint16 | Read/Write
678 | 1 | 844 | 2 | Data_reg 3_Node10 |  |  | uint16 | Read/Write
679 | 1 | 846 | 2 | Data_numReg 3_Node10 |  |  | uint16 | Read/Write
680 | 2 | 848 | 4 | Delta_Current_Node10 |  |  | float | Read/Write
682 | 2 | 852 | 4 | Offset_Current_Node10 |  |  | float | Read/Write
684 | 2 | 856 | 4 | CutOff_Node10 |  |  | float | Read/Write
686 | 2 | 860 | 4 | CT_Node10 |  |  | float | Read/Write
688 | 12 | 864 | 24 | Reserve_regs_Node10 |  |  |  | Read/Write
700 | 1 | 888 | 2 | Update_enable_Node11 |  |  | hex | Read/Write
701 | 1 | 890 | 2 | Cycle_wakeup_Node11 |  |  | uint16 | Read/Write
702 | 1 | 892 | 2 | Cycle_heathsta_Node11 |  |  | uint16 | Read/Write
703 | 1 | 894 | 2 | Data_numblock_Node11 |  |  | uint16 | Read/Write
704 | 1 | 896 | 2 | Data_reg 1_Node11 |  |  | uint16 | Read/Write
705 | 1 | 898 | 2 | Data_numreg 1_Node11 |  |  | uint16 | Read/Write
706 | 1 | 900 | 2 | Data_reg 2_Node11 |  |  | uint16 | Read/Write
707 | 1 | 902 | 2 | Data_numReg 2_Node11 |  |  | uint16 | Read/Write
708 | 1 | 904 | 2 | Data_reg 3_Node11 |  |  | uint16 | Read/Write
709 | 1 | 906 | 2 | Data_numReg 3_Node11 |  |  | uint16 | Read/Write
710 | 2 | 908 | 4 | Delta_Current_Node11 |  |  | float | Read/Write
712 | 2 | 912 | 4 | Offset_Current_Node11 |  |  | float | Read/Write
714 | 2 | 916 | 4 | CutOff_Node11 |  |  | float | Read/Write
716 | 2 | 920 | 4 | CT_Node11 |  |  | float | Read/Write
718 | 12 | 924 | 24 | Reserve_regs_Node11 |  |  |  | Read/Write
730 | 1 | 948 | 2 | Update_enable_Node12 |  |  | hex | Read/Write
731 | 1 | 950 | 2 | Cycle_wakeup_Node12 |  |  | uint16 | Read/Write
732 | 1 | 952 | 2 | Cycle_heathsta_Node12 |  |  | uint16 | Read/Write
733 | 1 | 954 | 2 | Data_numblock_Node12 |  |  | uint16 | Read/Write
734 | 1 | 956 | 2 | Data_reg 1_Node12 |  |  | uint16 | Read/Write
735 | 1 | 958 | 2 | Data_numreg 1_Node12 |  |  | uint16 | Read/Write
736 | 1 | 960 | 2 | Data_reg 2_Node12 |  |  | uint16 | Read/Write
737 | 1 | 962 | 2 | Data_numReg 2_Node12 |  |  | uint16 | Read/Write
738 | 1 | 964 | 2 | Data_reg 3_Node12 |  |  | uint16 | Read/Write
739 | 1 | 966 | 2 | Data_numReg 3_Node12 |  |  | uint16 | Read/Write
740 | 2 | 968 | 4 | Delta_Current_Node12 |  |  | float | Read/Write
742 | 2 | 972 | 4 | Offset_Current_Node12 |  |  | float | Read/Write
744 | 2 | 976 | 4 | CutOff_Node12 |  |  | float | Read/Write
746 | 2 | 980 | 4 | CT_Node12 |  |  | float | Read/Write
748 | 12 | 984 | 24 | Reserve_regs_Node12 |  |  |  | Read/Write
760 | 1 | 1008 | 2 | Update_enable_Node13 |  |  | hex | Read/Write
761 | 1 | 1010 | 2 | Cycle_wakeup_Node13 |  |  | uint16 | Read/Write
762 | 1 | 1012 | 2 | Cycle_heathsta_Node13 |  |  | uint16 | Read/Write
763 | 1 | 1014 | 2 | Data_numblock_Node13 |  |  | uint16 | Read/Write
764 | 1 | 1016 | 2 | Data_reg 1_Node13 |  |  | uint16 | Read/Write
765 | 1 | 1018 | 2 | Data_numreg 1_Node13 |  |  | uint16 | Read/Write
766 | 1 | 1020 | 2 | Data_reg 2_Node13 |  |  | uint16 | Read/Write
767 | 1 | 1022 | 2 | Data_numReg 2_Node13 |  |  | uint16 | Read/Write
768 | 1 | 1024 | 2 | Data_reg 3_Node13 |  |  | uint16 | Read/Write
769 | 1 | 1026 | 2 | Data_numReg 3_Node13 |  |  | uint16 | Read/Write
770 | 2 | 1028 | 4 | Delta_Current_Node13 |  |  | float | Read/Write
772 | 2 | 1032 | 4 | Offset_Current_Node13 |  |  | float | Read/Write
774 | 2 | 1036 | 4 | CutOff_Node13 |  |  | float | Read/Write
776 | 2 | 1040 | 4 | CT_Node13 |  |  | float | Read/Write
778 | 12 | 1044 | 24 | Reserve_regs_Node13 |  |  |  | Read/Write
790 | 1 | 1068 | 2 | Update_enable_Node14 |  |  | hex | Read/Write
791 | 1 | 1070 | 2 | Cycle_wakeup_Node14 |  |  | uint16 | Read/Write
792 | 1 | 1072 | 2 | Cycle_heathsta_Node14 |  |  | uint16 | Read/Write
793 | 1 | 1074 | 2 | Data_numblock_Node14 |  |  | uint16 | Read/Write
794 | 1 | 1076 | 2 | Data_reg 1_Node14 |  |  | uint16 | Read/Write
795 | 1 | 1078 | 2 | Data_numreg 1_Node14 |  |  | uint16 | Read/Write
796 | 1 | 1080 | 2 | Data_reg 2_Node14 |  |  | uint16 | Read/Write
797 | 1 | 1082 | 2 | Data_numReg 2_Node14 |  |  | uint16 | Read/Write
798 | 1 | 1084 | 2 | Data_reg 3_Node14 |  |  | uint16 | Read/Write
799 | 1 | 1086 | 2 | Data_numReg 3_Node14 |  |  | uint16 | Read/Write
800 | 2 | 1088 | 4 | Delta_Current_Node14 |  |  | float | Read/Write
802 | 2 | 1092 | 4 | Offset_Current_Node14 |  |  | float | Read/Write
804 | 2 | 1096 | 4 | CutOff_Node14 |  |  | float | Read/Write
806 | 2 | 1100 | 4 | CT_Node14 |  |  | float | Read/Write
808 | 12 | 1104 | 24 | Reserve_regs_Node14 |  |  |  | Read/Write
820 | 1 | 1128 | 2 | Update_enable_Node15 |  |  | hex | Read/Write
821 | 1 | 1130 | 2 | Cycle_wakeup_Node15 |  |  | uint16 | Read/Write
822 | 1 | 1132 | 2 | Cycle_heathsta_Node15 |  |  | uint16 | Read/Write
823 | 1 | 1134 | 2 | Data_numblock_Node15 |  |  | uint16 | Read/Write
824 | 1 | 1136 | 2 | Data_reg 1_Node15 |  |  | uint16 | Read/Write
825 | 1 | 1138 | 2 | Data_numreg 1_Node15 |  |  | uint16 | Read/Write
826 | 1 | 1140 | 2 | Data_reg 2_Node15 |  |  | uint16 | Read/Write
827 | 1 | 1142 | 2 | Data_numReg 2_Node15 |  |  | uint16 | Read/Write
828 | 1 | 1144 | 2 | Data_reg 3_Node15 |  |  | uint16 | Read/Write
829 | 1 | 1146 | 2 | Data_numReg 3_Node15 |  |  | uint16 | Read/Write
830 | 2 | 1148 | 4 | Delta_Current_Node15 |  |  | float | Read/Write
832 | 2 | 1152 | 4 | Offset_Current_Node15 |  |  | float | Read/Write
834 | 2 | 1156 | 4 | CutOff_Node15 |  |  | float | Read/Write
836 | 2 | 1160 | 4 | CT_Node15 |  |  | float | Read/Write
838 | 12 | 1164 | 24 | Reserve_regs_Node15 |  |  |  | Read/Write
850 | 1 | 1188 | 2 | Update_enable_Node16 |  |  | hex | Read/Write
851 | 1 | 1190 | 2 | Cycle_wakeup_Node16 |  |  | uint16 | Read/Write
852 | 1 | 1192 | 2 | Cycle_heathsta_Node16 |  |  | uint16 | Read/Write
853 | 1 | 1194 | 2 | Data_numblock_Node16 |  |  | uint16 | Read/Write
854 | 1 | 1196 | 2 | Data_reg 1_Node16 |  |  | uint16 | Read/Write
855 | 1 | 1198 | 2 | Data_numreg 1_Node16 |  |  | uint16 | Read/Write
856 | 1 | 1200 | 2 | Data_reg 2_Node16 |  |  | uint16 | Read/Write
857 | 1 | 1202 | 2 | Data_numReg 2_Node16 |  |  | uint16 | Read/Write
858 | 1 | 1204 | 2 | Data_reg 3_Node16 |  |  | uint16 | Read/Write
859 | 1 | 1206 | 2 | Data_numReg 3_Node16 |  |  | uint16 | Read/Write
860 | 2 | 1208 | 4 | Delta_Current_Node16 |  |  | float | Read/Write
862 | 2 | 1212 | 4 | Offset_Current_Node16 |  |  | float | Read/Write
864 | 2 | 1216 | 4 | CutOff_Node16 |  |  | float | Read/Write
866 | 2 | 1220 | 4 | CT_Node16 |  |  | float | Read/Write
868 | 12 | 1224 | 24 | Reserve_regs_Node16 |  |  |  | Read/Write
880 | 1 | 1248 | 2 | Update_enable_Node17 |  |  | hex | Read/Write
881 | 1 | 1250 | 2 | Cycle_wakeup_Node17 |  |  | uint16 | Read/Write
882 | 1 | 1252 | 2 | Cycle_heathsta_Node17 |  |  | uint16 | Read/Write
883 | 1 | 1254 | 2 | Data_numblock_Node17 |  |  | uint16 | Read/Write
884 | 1 | 1256 | 2 | Data_reg 1_Node17 |  |  | uint16 | Read/Write
885 | 1 | 1258 | 2 | Data_numreg 1_Node17 |  |  | uint16 | Read/Write
886 | 1 | 1260 | 2 | Data_reg 2_Node17 |  |  | uint16 | Read/Write
887 | 1 | 1262 | 2 | Data_numReg 2_Node17 |  |  | uint16 | Read/Write
888 | 1 | 1264 | 2 | Data_reg 3_Node17 |  |  | uint16 | Read/Write
889 | 1 | 1266 | 2 | Data_numReg 3_Node17 |  |  | uint16 | Read/Write
890 | 2 | 1268 | 4 | Delta_Current_Node17 |  |  | float | Read/Write
892 | 2 | 1272 | 4 | Offset_Current_Node17 |  |  | float | Read/Write
894 | 2 | 1276 | 4 | CutOff_Node17 |  |  | float | Read/Write
896 | 2 | 1280 | 4 | CT_Node17 |  |  | float | Read/Write
898 | 12 | 1284 | 24 | Reserve_regs_Node17 |  |  |  | Read/Write
910 | 1 | 1308 | 2 | Update_enable_Node18 |  |  | hex | Read/Write
911 | 1 | 1310 | 2 | Cycle_wakeup_Node18 |  |  | uint16 | Read/Write
912 | 1 | 1312 | 2 | Cycle_heathsta_Node18 |  |  | uint16 | Read/Write
913 | 1 | 1314 | 2 | Data_numblock_Node18 |  |  | uint16 | Read/Write
914 | 1 | 1316 | 2 | Data_reg 1_Node18 |  |  | uint16 | Read/Write
915 | 1 | 1318 | 2 | Data_numreg 1_Node18 |  |  | uint16 | Read/Write
916 | 1 | 1320 | 2 | Data_reg 2_Node18 |  |  | uint16 | Read/Write
917 | 1 | 1322 | 2 | Data_numReg 2_Node18 |  |  | uint16 | Read/Write
918 | 1 | 1324 | 2 | Data_reg 3_Node18 |  |  | uint16 | Read/Write
919 | 1 | 1326 | 2 | Data_numReg 3_Node18 |  |  | uint16 | Read/Write
920 | 2 | 1328 | 4 | Delta_Current_Node18 |  |  | float | Read/Write
922 | 2 | 1332 | 4 | Offset_Current_Node18 |  |  | float | Read/Write
924 | 2 | 1336 | 4 | CutOff_Node18 |  |  | float | Read/Write
926 | 2 | 1340 | 4 | CT_Node18 |  |  | float | Read/Write
928 | 12 | 1344 | 24 | Reserve_regs_Node18 |  |  |  | Read/Write
940 | 1 | 1368 | 2 | Update_enable_Node19 |  |  | hex | Read/Write
941 | 1 | 1370 | 2 | Cycle_wakeup_Node19 |  |  | uint16 | Read/Write
942 | 1 | 1372 | 2 | Cycle_heathsta_Node19 |  |  | uint16 | Read/Write
943 | 1 | 1374 | 2 | Data_numblock_Node19 |  |  | uint16 | Read/Write
944 | 1 | 1376 | 2 | Data_reg 1_Node19 |  |  | uint16 | Read/Write
945 | 1 | 1378 | 2 | Data_numreg 1_Node19 |  |  | uint16 | Read/Write
946 | 1 | 1380 | 2 | Data_reg 2_Node19 |  |  | uint16 | Read/Write
947 | 1 | 1382 | 2 | Data_numReg 2_Node19 |  |  | uint16 | Read/Write
948 | 1 | 1384 | 2 | Data_reg 3_Node19 |  |  | uint16 | Read/Write
949 | 1 | 1386 | 2 | Data_numReg 3_Node19 |  |  | uint16 | Read/Write
950 | 2 | 1388 | 4 | Delta_Current_Node19 |  |  | float | Read/Write
952 | 2 | 1392 | 4 | Offset_Current_Node19 |  |  | float | Read/Write
954 | 2 | 1396 | 4 | CutOff_Node19 |  |  | float | Read/Write
956 | 2 | 1400 | 4 | CT_Node19 |  |  | float | Read/Write
958 | 12 | 1404 | 24 | Reserve_regs_Node19 |  |  |  | Read/Write
970 | 1 | 1428 | 2 | Update_enable_Node20 |  |  | hex | Read/Write
971 | 1 | 1430 | 2 | Cycle_wakeup_Node20 |  |  | uint16 | Read/Write
972 | 1 | 1432 | 2 | Cycle_heathsta_Node20 |  |  | uint16 | Read/Write
973 | 1 | 1434 | 2 | Data_numblock_Node20 |  |  | uint16 | Read/Write
974 | 1 | 1436 | 2 | Data_reg 1_Node20 |  |  | uint16 | Read/Write
975 | 1 | 1438 | 2 | Data_numreg 1_Node20 |  |  | uint16 | Read/Write
976 | 1 | 1440 | 2 | Data_reg 2_Node20 |  |  | uint16 | Read/Write
977 | 1 | 1442 | 2 | Data_numReg 2_Node20 |  |  | uint16 | Read/Write
978 | 1 | 1444 | 2 | Data_reg 3_Node20 |  |  | uint16 | Read/Write
979 | 1 | 1446 | 2 | Data_numReg 3_Node20 |  |  | uint16 | Read/Write
980 | 2 | 1448 | 4 | Delta_Current_Node20 |  |  | float | Read/Write
982 | 2 | 1452 | 4 | Offset_Current_Node20 |  |  | float | Read/Write
984 | 2 | 1456 | 4 | CutOff_Node20 |  |  | float | Read/Write
986 | 2 | 1460 | 4 | CT_Node20 |  |  | float | Read/Write
988 | 12 | 1464 | 24 | Reserve_regs_Node20 |  |  |  | Read/Write
1000 | 1 | 1488 | 2 | Update_enable_Node21 |  |  | hex | Read/Write
1001 | 1 | 1490 | 2 | Cycle_wakeup_Node21 |  |  | uint16 | Read/Write
1002 | 1 | 1492 | 2 | Cycle_heathsta_Node21 |  |  | uint16 | Read/Write
1003 | 1 | 1494 | 2 | Data_numblock_Node21 |  |  | uint16 | Read/Write
1004 | 1 | 1496 | 2 | Data_reg 1_Node21 |  |  | uint16 | Read/Write
1005 | 1 | 1498 | 2 | Data_numreg 1_Node21 |  |  | uint16 | Read/Write
1006 | 1 | 1500 | 2 | Data_reg 2_Node21 |  |  | uint16 | Read/Write
1007 | 1 | 1502 | 2 | Data_numReg 2_Node21 |  |  | uint16 | Read/Write
1008 | 1 | 1504 | 2 | Data_reg 3_Node21 |  |  | uint16 | Read/Write
1009 | 1 | 1506 | 2 | Data_numReg 3_Node21 |  |  | uint16 | Read/Write
1010 | 2 | 1508 | 4 | Delta_Current_Node21 |  |  | float | Read/Write
1012 | 2 | 1512 | 4 | Offset_Current_Node21 |  |  | float | Read/Write
1014 | 2 | 1516 | 4 | CutOff_Node21 |  |  | float | Read/Write
1016 | 2 | 1520 | 4 | CT_Node21 |  |  | float | Read/Write
1018 | 12 | 1524 | 24 | Reserve_regs_Node21 |  |  |  | Read/Write
1030 | 1 | 1548 | 2 | Update_enable_Node22 |  |  | hex | Read/Write
1031 | 1 | 1550 | 2 | Cycle_wakeup_Node22 |  |  | uint16 | Read/Write
1032 | 1 | 1552 | 2 | Cycle_heathsta_Node22 |  |  | uint16 | Read/Write
1033 | 1 | 1554 | 2 | Data_numblock_Node22 |  |  | uint16 | Read/Write
1034 | 1 | 1556 | 2 | Data_reg 1_Node22 |  |  | uint16 | Read/Write
1035 | 1 | 1558 | 2 | Data_numreg 1_Node22 |  |  | uint16 | Read/Write
1036 | 1 | 1560 | 2 | Data_reg 2_Node22 |  |  | uint16 | Read/Write
1037 | 1 | 1562 | 2 | Data_numReg 2_Node22 |  |  | uint16 | Read/Write
1038 | 1 | 1564 | 2 | Data_reg 3_Node22 |  |  | uint16 | Read/Write
1039 | 1 | 1566 | 2 | Data_numReg 3_Node22 |  |  | uint16 | Read/Write
1040 | 2 | 1568 | 4 | Delta_Current_Node22 |  |  | float | Read/Write
1042 | 2 | 1572 | 4 | Offset_Current_Node22 |  |  | float | Read/Write
1044 | 2 | 1576 | 4 | CutOff_Node22 |  |  | float | Read/Write
1046 | 2 | 1580 | 4 | CT_Node22 |  |  | float | Read/Write
1048 | 12 | 1584 | 24 | Reserve_regs_Node22 |  |  |  | Read/Write
1060 | 1 | 1608 | 2 | Update_enable_Node23 |  |  | hex | Read/Write
1061 | 1 | 1610 | 2 | Cycle_wakeup_Node23 |  |  | uint16 | Read/Write
1062 | 1 | 1612 | 2 | Cycle_heathsta_Node23 |  |  | uint16 | Read/Write
1063 | 1 | 1614 | 2 | Data_numblock_Node23 |  |  | uint16 | Read/Write
1064 | 1 | 1616 | 2 | Data_reg 1_Node23 |  |  | uint16 | Read/Write
1065 | 1 | 1618 | 2 | Data_numreg 1_Node23 |  |  | uint16 | Read/Write
1066 | 1 | 1620 | 2 | Data_reg 2_Node23 |  |  | uint16 | Read/Write
1067 | 1 | 1622 | 2 | Data_numReg 2_Node23 |  |  | uint16 | Read/Write
1068 | 1 | 1624 | 2 | Data_reg 3_Node23 |  |  | uint16 | Read/Write
1069 | 1 | 1626 | 2 | Data_numReg 3_Node23 |  |  | uint16 | Read/Write
1070 | 2 | 1628 | 4 | Delta_Current_Node23 |  |  | float | Read/Write
1072 | 2 | 1632 | 4 | Offset_Current_Node23 |  |  | float | Read/Write
1074 | 2 | 1636 | 4 | CutOff_Node23 |  |  | float | Read/Write
1076 | 2 | 1640 | 4 | CT_Node23 |  |  | float | Read/Write
1078 | 12 | 1644 | 24 | Reserve_regs_Node23 |  |  |  | Read/Write
1090 | 1 | 1668 | 2 | Update_enable_Node24 |  |  | hex | Read/Write
1091 | 1 | 1670 | 2 | Cycle_wakeup_Node24 |  |  | uint16 | Read/Write
1092 | 1 | 1672 | 2 | Cycle_heathsta_Node24 |  |  | uint16 | Read/Write
1093 | 1 | 1674 | 2 | Data_numblock_Node24 |  |  | uint16 | Read/Write
1094 | 1 | 1676 | 2 | Data_reg 1_Node24 |  |  | uint16 | Read/Write
1095 | 1 | 1678 | 2 | Data_numreg 1_Node24 |  |  | uint16 | Read/Write
1096 | 1 | 1680 | 2 | Data_reg 2_Node24 |  |  | uint16 | Read/Write
1097 | 1 | 1682 | 2 | Data_numReg 2_Node24 |  |  | uint16 | Read/Write
1098 | 1 | 1684 | 2 | Data_reg 3_Node24 |  |  | uint16 | Read/Write
1099 | 1 | 1686 | 2 | Data_numReg 3_Node24 |  |  | uint16 | Read/Write
1100 | 2 | 1688 | 4 | Delta_Current_Node24 |  |  | float | Read/Write
1102 | 2 | 1692 | 4 | Offset_Current_Node24 |  |  | float | Read/Write
1104 | 2 | 1696 | 4 | CutOff_Node24 |  |  | float | Read/Write
1106 | 2 | 1700 | 4 | CT_Node24 |  |  | float | Read/Write
1108 | 12 | 1704 | 24 | Reserve_regs_Node24 |  |  |  | Read/Write
1120 | 1 | 1728 | 2 | Update_enable_Node25 |  |  | hex | Read/Write
1121 | 1 | 1730 | 2 | Cycle_wakeup_Node25 |  |  | uint16 | Read/Write
1122 | 1 | 1732 | 2 | Cycle_heathsta_Node25 |  |  | uint16 | Read/Write
1123 | 1 | 1734 | 2 | Data_numblock_Node25 |  |  | uint16 | Read/Write
1124 | 1 | 1736 | 2 | Data_reg 1_Node25 |  |  | uint16 | Read/Write
1125 | 1 | 1738 | 2 | Data_numreg 1_Node25 |  |  | uint16 | Read/Write
1126 | 1 | 1740 | 2 | Data_reg 2_Node25 |  |  | uint16 | Read/Write
1127 | 1 | 1742 | 2 | Data_numReg 2_Node25 |  |  | uint16 | Read/Write
1128 | 1 | 1744 | 2 | Data_reg 3_Node25 |  |  | uint16 | Read/Write
1129 | 1 | 1746 | 2 | Data_numReg 3_Node25 |  |  | uint16 | Read/Write
1130 | 2 | 1748 | 4 | Delta_Current_Node25 |  |  | float | Read/Write
1132 | 2 | 1752 | 4 | Offset_Current_Node25 |  |  | float | Read/Write
1134 | 2 | 1756 | 4 | CutOff_Node25 |  |  | float | Read/Write
1136 | 2 | 1760 | 4 | CT_Node25 |  |  | float | Read/Write
1138 | 12 | 1764 | 24 | Reserve_regs_Node25 |  |  |  | Read/Write
1150 | 1 | 1788 | 2 | Update_enable_Node26 |  |  | hex | Read/Write
1151 | 1 | 1790 | 2 | Cycle_wakeup_Node26 |  |  | uint16 | Read/Write
1152 | 1 | 1792 | 2 | Cycle_heathsta_Node26 |  |  | uint16 | Read/Write
1153 | 1 | 1794 | 2 | Data_numblock_Node26 |  |  | uint16 | Read/Write
1154 | 1 | 1796 | 2 | Data_reg 1_Node26 |  |  | uint16 | Read/Write
1155 | 1 | 1798 | 2 | Data_numreg 1_Node26 |  |  | uint16 | Read/Write
1156 | 1 | 1800 | 2 | Data_reg 2_Node26 |  |  | uint16 | Read/Write
1157 | 1 | 1802 | 2 | Data_numReg 2_Node26 |  |  | uint16 | Read/Write
1158 | 1 | 1804 | 2 | Data_reg 3_Node26 |  |  | uint16 | Read/Write
1159 | 1 | 1806 | 2 | Data_numReg 3_Node26 |  |  | uint16 | Read/Write
1160 | 2 | 1808 | 4 | Delta_Current_Node26 |  |  | float | Read/Write
1162 | 2 | 1812 | 4 | Offset_Current_Node26 |  |  | float | Read/Write
1164 | 2 | 1816 | 4 | CutOff_Node26 |  |  | float | Read/Write
1166 | 2 | 1820 | 4 | CT_Node26 |  |  | float | Read/Write
1168 | 12 | 1824 | 24 | Reserve_regs_Node26 |  |  |  | Read/Write
1180 | 1 | 1848 | 2 | Update_enable_Node27 |  |  | hex | Read/Write
1181 | 1 | 1850 | 2 | Cycle_wakeup_Node27 |  |  | uint16 | Read/Write
1182 | 1 | 1852 | 2 | Cycle_heathsta_Node27 |  |  | uint16 | Read/Write
1183 | 1 | 1854 | 2 | Data_numblock_Node27 |  |  | uint16 | Read/Write
1184 | 1 | 1856 | 2 | Data_reg 1_Node27 |  |  | uint16 | Read/Write
1185 | 1 | 1858 | 2 | Data_numreg 1_Node27 |  |  | uint16 | Read/Write
1186 | 1 | 1860 | 2 | Data_reg 2_Node27 |  |  | uint16 | Read/Write
1187 | 1 | 1862 | 2 | Data_numReg 2_Node27 |  |  | uint16 | Read/Write
1188 | 1 | 1864 | 2 | Data_reg 3_Node27 |  |  | uint16 | Read/Write
1189 | 1 | 1866 | 2 | Data_numReg 3_Node27 |  |  | uint16 | Read/Write
1190 | 2 | 1868 | 4 | Delta_Current_Node27 |  |  | float | Read/Write
1192 | 2 | 1872 | 4 | Offset_Current_Node27 |  |  | float | Read/Write
1194 | 2 | 1876 | 4 | CutOff_Node27 |  |  | float | Read/Write
1196 | 2 | 1880 | 4 | CT_Node27 |  |  | float | Read/Write
1198 | 12 | 1884 | 24 | Reserve_regs_Node27 |  |  |  | Read/Write
1210 | 1 | 1908 | 2 | Update_enable_Node28 |  |  | hex | Read/Write
1211 | 1 | 1910 | 2 | Cycle_wakeup_Node28 |  |  | uint16 | Read/Write
1212 | 1 | 1912 | 2 | Cycle_heathsta_Node28 |  |  | uint16 | Read/Write
1213 | 1 | 1914 | 2 | Data_numblock_Node28 |  |  | uint16 | Read/Write
1214 | 1 | 1916 | 2 | Data_reg 1_Node28 |  |  | uint16 | Read/Write
1215 | 1 | 1918 | 2 | Data_numreg 1_Node28 |  |  | uint16 | Read/Write
1216 | 1 | 1920 | 2 | Data_reg 2_Node28 |  |  | uint16 | Read/Write
1217 | 1 | 1922 | 2 | Data_numReg 2_Node28 |  |  | uint16 | Read/Write
1218 | 1 | 1924 | 2 | Data_reg 3_Node28 |  |  | uint16 | Read/Write
1219 | 1 | 1926 | 2 | Data_numReg 3_Node28 |  |  | uint16 | Read/Write
1220 | 2 | 1928 | 4 | Delta_Current_Node28 |  |  | float | Read/Write
1222 | 2 | 1932 | 4 | Offset_Current_Node28 |  |  | float | Read/Write
1224 | 2 | 1936 | 4 | CutOff_Node28 |  |  | float | Read/Write
1226 | 2 | 1940 | 4 | CT_Node28 |  |  | float | Read/Write
1228 | 12 | 1944 | 24 | Reserve_regs_Node28 |  |  |  | Read/Write
1240 | 1 | 1968 | 2 | Update_enable_Node29 |  |  | hex | Read/Write
1241 | 1 | 1970 | 2 | Cycle_wakeup_Node29 |  |  | uint16 | Read/Write
1242 | 1 | 1972 | 2 | Cycle_heathsta_Node29 |  |  | uint16 | Read/Write
1243 | 1 | 1974 | 2 | Data_numblock_Node29 |  |  | uint16 | Read/Write
1244 | 1 | 1976 | 2 | Data_reg 1_Node29 |  |  | uint16 | Read/Write
1245 | 1 | 1978 | 2 | Data_numreg 1_Node29 |  |  | uint16 | Read/Write
1246 | 1 | 1980 | 2 | Data_reg 2_Node29 |  |  | uint16 | Read/Write
1247 | 1 | 1982 | 2 | Data_numReg 2_Node29 |  |  | uint16 | Read/Write
1248 | 1 | 1984 | 2 | Data_reg 3_Node29 |  |  | uint16 | Read/Write
1249 | 1 | 1986 | 2 | Data_numReg 3_Node29 |  |  | uint16 | Read/Write
1250 | 2 | 1988 | 4 | Delta_Current_Node29 |  |  | float | Read/Write
1252 | 2 | 1992 | 4 | Offset_Current_Node29 |  |  | float | Read/Write
1254 | 2 | 1996 | 4 | CutOff_Node29 |  |  | float | Read/Write
1256 | 2 | 2000 | 4 | CT_Node29 |  |  | float | Read/Write
1258 | 12 | 2004 | 24 | Reserve_regs_Node29 |  |  |  | Read/Write
1270 | 1 | 2028 | 2 | Update_enable_Node30 |  |  | hex | Read/Write
1271 | 1 | 2030 | 2 | Cycle_wakeup_Node30 |  |  | uint16 | Read/Write
1272 | 1 | 2032 | 2 | Cycle_heathsta_Node30 |  |  | uint16 | Read/Write
1273 | 1 | 2034 | 2 | Data_numblock_Node30 |  |  | uint16 | Read/Write
1274 | 1 | 2036 | 2 | Data_reg 1_Node30 |  |  | uint16 | Read/Write
1275 | 1 | 2038 | 2 | Data_numreg 1_Node30 |  |  | uint16 | Read/Write
1276 | 1 | 2040 | 2 | Data_reg 2_Node30 |  |  | uint16 | Read/Write
1277 | 1 | 2042 | 2 | Data_numReg 2_Node30 |  |  | uint16 | Read/Write
1278 | 1 | 2044 | 2 | Data_reg 3_Node30 |  |  | uint16 | Read/Write
1279 | 1 | 2046 | 2 | Data_numReg 3_Node30 |  |  | uint16 | Read/Write
1280 | 2 | 2048 | 4 | Delta_Current_Node30 |  |  | float | Read/Write
1282 | 2 | 2052 | 4 | Offset_Current_Node30 |  |  | float | Read/Write
1284 | 2 | 2056 | 4 | CutOff_Node30 |  |  | float | Read/Write
1286 | 2 | 2060 | 4 | CT_Node30 |  |  | float | Read/Write
1288 | 12 | 2064 | 24 | Reserve_regs_Node30 |  |  |  | Read/Write
1300 | 1 | 2088 | 2 | Update_enable_Node31 |  |  | hex | Read/Write
1301 | 1 | 2090 | 2 | Cycle_wakeup_Node31 |  |  | uint16 | Read/Write
1302 | 1 | 2092 | 2 | Cycle_heathsta_Node31 |  |  | uint16 | Read/Write
1303 | 1 | 2094 | 2 | Data_numblock_Node31 |  |  | uint16 | Read/Write
1304 | 1 | 2096 | 2 | Data_reg 1_Node31 |  |  | uint16 | Read/Write
1305 | 1 | 2098 | 2 | Data_numreg 1_Node31 |  |  | uint16 | Read/Write
1306 | 1 | 2100 | 2 | Data_reg 2_Node31 |  |  | uint16 | Read/Write
1307 | 1 | 2102 | 2 | Data_numReg 2_Node31 |  |  | uint16 | Read/Write
1308 | 1 | 2104 | 2 | Data_reg 3_Node31 |  |  | uint16 | Read/Write
1309 | 1 | 2106 | 2 | Data_numReg 3_Node31 |  |  | uint16 | Read/Write
1310 | 2 | 2108 | 4 | Delta_Current_Node31 |  |  | float | Read/Write
1312 | 2 | 2112 | 4 | Offset_Current_Node31 |  |  | float | Read/Write
1314 | 2 | 2116 | 4 | CutOff_Node31 |  |  | float | Read/Write
1316 | 2 | 2120 | 4 | CT_Node31 |  |  | float | Read/Write
1318 | 12 | 2124 | 24 | Reserve_regs_Node31 |  |  |  | Read/Write
1330 | 1 | 2148 | 2 | Update_enable_Node32 |  |  | hex | Read/Write
1331 | 1 | 2150 | 2 | Cycle_wakeup_Node32 |  |  | uint16 | Read/Write
1332 | 1 | 2152 | 2 | Cycle_heathsta_Node32 |  |  | uint16 | Read/Write
1333 | 1 | 2154 | 2 | Data_numblock_Node32 |  |  | uint16 | Read/Write
1334 | 1 | 2156 | 2 | Data_reg 1_Node32 |  |  | uint16 | Read/Write
1335 | 1 | 2158 | 2 | Data_numreg 1_Node32 |  |  | uint16 | Read/Write
1336 | 1 | 2160 | 2 | Data_reg 2_Node32 |  |  | uint16 | Read/Write
1337 | 1 | 2162 | 2 | Data_numReg 2_Node32 |  |  | uint16 | Read/Write
1338 | 1 | 2164 | 2 | Data_reg 3_Node32 |  |  | uint16 | Read/Write
1339 | 1 | 2166 | 2 | Data_numReg 3_Node32 |  |  | uint16 | Read/Write
1340 | 2 | 2168 | 4 | Delta_Current_Node32 |  |  | float | Read/Write
1342 | 2 | 2172 | 4 | Offset_Current_Node32 |  |  | float | Read/Write
1344 | 2 | 2176 | 4 | CutOff_Node32 |  |  | float | Read/Write
1346 | 2 | 2180 | 4 | CT_Node32 |  |  | float | Read/Write
1348 | 12 | 2184 | 24 | Reserve_regs_Node32 |  |  |  | Read/Write
1360 | 1 | 2208 | 2 | Update_enable_Node33 |  |  | hex | Read/Write
1361 | 1 | 2210 | 2 | Cycle_wakeup_Node33 |  |  | uint16 | Read/Write
1362 | 1 | 2212 | 2 | Cycle_heathsta_Node33 |  |  | uint16 | Read/Write
1363 | 1 | 2214 | 2 | Data_numblock_Node33 |  |  | uint16 | Read/Write
1364 | 1 | 2216 | 2 | Data_reg 1_Node33 |  |  | uint16 | Read/Write
1365 | 1 | 2218 | 2 | Data_numreg 1_Node33 |  |  | uint16 | Read/Write
1366 | 1 | 2220 | 2 | Data_reg 2_Node33 |  |  | uint16 | Read/Write
1367 | 1 | 2222 | 2 | Data_numReg 2_Node33 |  |  | uint16 | Read/Write
1368 | 1 | 2224 | 2 | Data_reg 3_Node33 |  |  | uint16 | Read/Write
1369 | 1 | 2226 | 2 | Data_numReg 3_Node33 |  |  | uint16 | Read/Write
1370 | 2 | 2228 | 4 | Delta_Current_Node33 |  |  | float | Read/Write
1372 | 2 | 2232 | 4 | Offset_Current_Node33 |  |  | float | Read/Write
1374 | 2 | 2236 | 4 | CutOff_Node33 |  |  | float | Read/Write
1376 | 2 | 2240 | 4 | CT_Node33 |  |  | float | Read/Write
1378 | 12 | 2244 | 24 | Reserve_regs_Node33 |  |  |  | Read/Write
1390 | 1 | 2268 | 2 | Update_enable_Node34 |  |  | hex | Read/Write
1391 | 1 | 2270 | 2 | Cycle_wakeup_Node34 |  |  | uint16 | Read/Write
1392 | 1 | 2272 | 2 | Cycle_heathsta_Node34 |  |  | uint16 | Read/Write
1393 | 1 | 2274 | 2 | Data_numblock_Node34 |  |  | uint16 | Read/Write
1394 | 1 | 2276 | 2 | Data_reg 1_Node34 |  |  | uint16 | Read/Write
1395 | 1 | 2278 | 2 | Data_numreg 1_Node34 |  |  | uint16 | Read/Write
1396 | 1 | 2280 | 2 | Data_reg 2_Node34 |  |  | uint16 | Read/Write
1397 | 1 | 2282 | 2 | Data_numReg 2_Node34 |  |  | uint16 | Read/Write
1398 | 1 | 2284 | 2 | Data_reg 3_Node34 |  |  | uint16 | Read/Write
1399 | 1 | 2286 | 2 | Data_numReg 3_Node34 |  |  | uint16 | Read/Write
1400 | 2 | 2288 | 4 | Delta_Current_Node34 |  |  | float | Read/Write
1402 | 2 | 2292 | 4 | Offset_Current_Node34 |  |  | float | Read/Write
1404 | 2 | 2296 | 4 | CutOff_Node34 |  |  | float | Read/Write
1406 | 2 | 2300 | 4 | CT_Node34 |  |  | float | Read/Write
1408 | 12 | 2304 | 24 | Reserve_regs_Node34 |  |  |  | Read/Write
1420 | 1 | 2328 | 2 | Update_enable_Node35 |  |  | hex | Read/Write
1421 | 1 | 2330 | 2 | Cycle_wakeup_Node35 |  |  | uint16 | Read/Write
1422 | 1 | 2332 | 2 | Cycle_heathsta_Node35 |  |  | uint16 | Read/Write
1423 | 1 | 2334 | 2 | Data_numblock_Node35 |  |  | uint16 | Read/Write
1424 | 1 | 2336 | 2 | Data_reg 1_Node35 |  |  | uint16 | Read/Write
1425 | 1 | 2338 | 2 | Data_numreg 1_Node35 |  |  | uint16 | Read/Write
1426 | 1 | 2340 | 2 | Data_reg 2_Node35 |  |  | uint16 | Read/Write
1427 | 1 | 2342 | 2 | Data_numReg 2_Node35 |  |  | uint16 | Read/Write
1428 | 1 | 2344 | 2 | Data_reg 3_Node35 |  |  | uint16 | Read/Write
1429 | 1 | 2346 | 2 | Data_numReg 3_Node35 |  |  | uint16 | Read/Write
1430 | 2 | 2348 | 4 | Delta_Current_Node35 |  |  | float | Read/Write
1432 | 2 | 2352 | 4 | Offset_Current_Node35 |  |  | float | Read/Write
1434 | 2 | 2356 | 4 | CutOff_Node35 |  |  | float | Read/Write
1436 | 2 | 2360 | 4 | CT_Node35 |  |  | float | Read/Write
1438 | 12 | 2364 | 24 | Reserve_regs_Node35 |  |  |  | Read/Write
1450 | 1 | 2388 | 2 | Update_enable_Node36 |  |  | hex | Read/Write
1451 | 1 | 2390 | 2 | Cycle_wakeup_Node36 |  |  | uint16 | Read/Write
1452 | 1 | 2392 | 2 | Cycle_heathsta_Node36 |  |  | uint16 | Read/Write
1453 | 1 | 2394 | 2 | Data_numblock_Node36 |  |  | uint16 | Read/Write
1454 | 1 | 2396 | 2 | Data_reg 1_Node36 |  |  | uint16 | Read/Write
1455 | 1 | 2398 | 2 | Data_numreg 1_Node36 |  |  | uint16 | Read/Write
1456 | 1 | 2400 | 2 | Data_reg 2_Node36 |  |  | uint16 | Read/Write
1457 | 1 | 2402 | 2 | Data_numReg 2_Node36 |  |  | uint16 | Read/Write
1458 | 1 | 2404 | 2 | Data_reg 3_Node36 |  |  | uint16 | Read/Write
1459 | 1 | 2406 | 2 | Data_numReg 3_Node36 |  |  | uint16 | Read/Write
1460 | 2 | 2408 | 4 | Delta_Current_Node36 |  |  | float | Read/Write
1462 | 2 | 2412 | 4 | Offset_Current_Node36 |  |  | float | Read/Write
1464 | 2 | 2416 | 4 | CutOff_Node36 |  |  | float | Read/Write
1466 | 2 | 2420 | 4 | CT_Node36 |  |  | float | Read/Write
1468 | 12 | 2424 | 24 | Reserve_regs_Node36 |  |  |  | Read/Write
1480 | 1 | 2448 | 2 | Update_enable_Node37 |  |  | hex | Read/Write
1481 | 1 | 2450 | 2 | Cycle_wakeup_Node37 |  |  | uint16 | Read/Write
1482 | 1 | 2452 | 2 | Cycle_heathsta_Node37 |  |  | uint16 | Read/Write
1483 | 1 | 2454 | 2 | Data_numblock_Node37 |  |  | uint16 | Read/Write
1484 | 1 | 2456 | 2 | Data_reg 1_Node37 |  |  | uint16 | Read/Write
1485 | 1 | 2458 | 2 | Data_numreg 1_Node37 |  |  | uint16 | Read/Write
1486 | 1 | 2460 | 2 | Data_reg 2_Node37 |  |  | uint16 | Read/Write
1487 | 1 | 2462 | 2 | Data_numReg 2_Node37 |  |  | uint16 | Read/Write
1488 | 1 | 2464 | 2 | Data_reg 3_Node37 |  |  | uint16 | Read/Write
1489 | 1 | 2466 | 2 | Data_numReg 3_Node37 |  |  | uint16 | Read/Write
1490 | 2 | 2468 | 4 | Delta_Current_Node37 |  |  | float | Read/Write
1492 | 2 | 2472 | 4 | Offset_Current_Node37 |  |  | float | Read/Write
1494 | 2 | 2476 | 4 | CutOff_Node37 |  |  | float | Read/Write
1496 | 2 | 2480 | 4 | CT_Node37 |  |  | float | Read/Write
1498 | 12 | 2484 | 24 | Reserve_regs_Node37 |  |  |  | Read/Write
1510 | 1 | 2508 | 2 | Update_enable_Node38 |  |  | hex | Read/Write
1511 | 1 | 2510 | 2 | Cycle_wakeup_Node38 |  |  | uint16 | Read/Write
1512 | 1 | 2512 | 2 | Cycle_heathsta_Node38 |  |  | uint16 | Read/Write
1513 | 1 | 2514 | 2 | Data_numblock_Node38 |  |  | uint16 | Read/Write
1514 | 1 | 2516 | 2 | Data_reg 1_Node38 |  |  | uint16 | Read/Write
1515 | 1 | 2518 | 2 | Data_numreg 1_Node38 |  |  | uint16 | Read/Write
1516 | 1 | 2520 | 2 | Data_reg 2_Node38 |  |  | uint16 | Read/Write
1517 | 1 | 2522 | 2 | Data_numReg 2_Node38 |  |  | uint16 | Read/Write
1518 | 1 | 2524 | 2 | Data_reg 3_Node38 |  |  | uint16 | Read/Write
1519 | 1 | 2526 | 2 | Data_numReg 3_Node38 |  |  | uint16 | Read/Write
1520 | 2 | 2528 | 4 | Delta_Current_Node38 |  |  | float | Read/Write
1522 | 2 | 2532 | 4 | Offset_Current_Node38 |  |  | float | Read/Write
1524 | 2 | 2536 | 4 | CutOff_Node38 |  |  | float | Read/Write
1526 | 2 | 2540 | 4 | CT_Node38 |  |  | float | Read/Write
1528 | 12 | 2544 | 24 | Reserve_regs_Node38 |  |  |  | Read/Write
1540 | 1 | 2568 | 2 | Update_enable_Node39 |  |  | hex | Read/Write
1541 | 1 | 2570 | 2 | Cycle_wakeup_Node39 |  |  | uint16 | Read/Write
1542 | 1 | 2572 | 2 | Cycle_heathsta_Node39 |  |  | uint16 | Read/Write
1543 | 1 | 2574 | 2 | Data_numblock_Node39 |  |  | uint16 | Read/Write
1544 | 1 | 2576 | 2 | Data_reg 1_Node39 |  |  | uint16 | Read/Write
1545 | 1 | 2578 | 2 | Data_numreg 1_Node39 |  |  | uint16 | Read/Write
1546 | 1 | 2580 | 2 | Data_reg 2_Node39 |  |  | uint16 | Read/Write
1547 | 1 | 2582 | 2 | Data_numReg 2_Node39 |  |  | uint16 | Read/Write
1548 | 1 | 2584 | 2 | Data_reg 3_Node39 |  |  | uint16 | Read/Write
1549 | 1 | 2586 | 2 | Data_numReg 3_Node39 |  |  | uint16 | Read/Write
1550 | 2 | 2588 | 4 | Delta_Current_Node39 |  |  | float | Read/Write
1552 | 2 | 2592 | 4 | Offset_Current_Node39 |  |  | float | Read/Write
1554 | 2 | 2596 | 4 | CutOff_Node39 |  |  | float | Read/Write
1556 | 2 | 2600 | 4 | CT_Node39 |  |  | float | Read/Write
1558 | 12 | 2604 | 24 | Reserve_regs_Node39 |  |  |  | Read/Write
1570 | 1 | 2628 | 2 | Update_enable_Node40 |  |  | hex | Read/Write
1571 | 1 | 2630 | 2 | Cycle_wakeup_Node40 |  |  | uint16 | Read/Write
1572 | 1 | 2632 | 2 | Cycle_heathsta_Node40 |  |  | uint16 | Read/Write
1573 | 1 | 2634 | 2 | Data_numblock_Node40 |  |  | uint16 | Read/Write
1574 | 1 | 2636 | 2 | Data_reg 1_Node40 |  |  | uint16 | Read/Write
1575 | 1 | 2638 | 2 | Data_numreg 1_Node40 |  |  | uint16 | Read/Write
1576 | 1 | 2640 | 2 | Data_reg 2_Node40 |  |  | uint16 | Read/Write
1577 | 1 | 2642 | 2 | Data_numReg 2_Node40 |  |  | uint16 | Read/Write
1578 | 1 | 2644 | 2 | Data_reg 3_Node40 |  |  | uint16 | Read/Write
1579 | 1 | 2646 | 2 | Data_numReg 3_Node40 |  |  | uint16 | Read/Write
1580 | 2 | 2648 | 4 | Delta_Current_Node40 |  |  | float | Read/Write
1582 | 2 | 2652 | 4 | Offset_Current_Node40 |  |  | float | Read/Write
1584 | 2 | 2656 | 4 | CutOff_Node40 |  |  | float | Read/Write
1586 | 2 | 2660 | 4 | CT_Node40 |  |  | float | Read/Write
1588 | 12 | 2664 | 24 | Reserve_regs_Node40 |  |  |  | Read/Write

## Sensor là Press. (hidden)
Modbus Register | # of register | Adr | Size | Description | Range | Default | Format | Property | Comment
41216 | 1 |  | 2 | %Battery Node1 | 10,30,60,99 |  | uint16 | Read | Wireless Sensor là loại cảm biến áp suất, 0xA100..0xA120
41217 | 2 |  | 4 | Pressure Node1 | % |  | float | Read | Pressure output = 0%..100%
41219 | 1 |  | 2 | Status Node1 | 0-255 |  | uint16 | Read | Byte Hi "error", byte lo "loại sensor": + byte lo = 1: cảm biến nhiệt độ + byte lo = 2: cảm biến độ ẩm + byte lo = 3: cảm biến chênh áp môi trường + byte lo = 4: cảm biến áp suất + byte lo = 5: cảm biến 1 kênh đo dòng AC + byte lo = 6: cảm biến digital input, 2 kênh Counter + byte lo = 7: cảm biến digital input, 2 kênh Status + byte lo = 8: cảm biến 2 kênh volts 3vdc + byte lo = 9: cảm biến 1 kênh 0-20mA + byte lo = 10: cảm biến ngõ ra 4 kênh relay SPST + byte lo = 11: cảm biến ngõ ra 2 kênh relay SPDT + byte lo = 12: cảm biến ánh sáng môi trường + byte lo = 255: không có cảm biến + byte hi = 0: không có lỗi + byte hi = 1: đã thay đổi loại sensor port M12F mà chưa reset để nhận dạng cảm biến mới + byte hi = 2: sensor port M12F chạm GND + byte hi = 3: sensor port M12F chạm Vcc + byte hi = 4: sensor port M12F chạm nhau + byte hi = 51: sensor port uart bị lỗi check sum
41220 | 2 |  | 4 | Temperature Node1 | oC |  | float | Read
41472 | 1 |  | 2 | %Battery Node2 | 10,30,60,99 |  | uint16 | Read | 0xA200..0xA220
41473 | 2 |  | 4 | Pressure Node2 | % |  | float | Read
41475 | 1 |  | 2 | Status Node2 | 0-255 |  | uint16 | Read
41476 | 2 |  | 4 | Temperature Node2 | oC |  | float | Read
41728 | 1 |  | 2 | %Battery Node3 | 10,30,60,99 |  | uint16 | Read | 0xA300..0xA320
41729 | 2 |  | 4 | Pressure Node3 | % |  | float | Read
41731 | 1 |  | 2 | Status Node3 | 0-255 |  | uint16 | Read
41732 | 2 |  | 4 | Temperature Node3 | oC |  | float | Read
41984 | 1 |  | 2 | %Battery Node4 | 10,30,60,99 |  | uint16 | Read | 0xA400..0xA420
41985 | 2 |  | 4 | Pressure Node4 | % |  | float | Read
41987 | 1 |  | 2 | Status Node4 | 0-255 |  | uint16 | Read
41988 | 2 |  | 4 | Temperature Node4 | oC |  | float | Read
42240 | 1 |  | 2 | %Battery Node5 | 10,30,60,99 |  | uint16 | Read | 0xA500..0xA520
42241 | 2 |  | 4 | Pressure Node5 | % |  | float | Read
42243 | 1 |  | 2 | Status Node5 | 0-255 |  | uint16 | Read
42244 | 2 |  | 4 | Temperature Node5 | oC |  | float | Read
42496 | 1 |  | 2 | %Battery Node6 | 10,30,60,99 |  | uint16 | Read | 0xA600..0xA620
42497 | 2 |  | 4 | Pressure Node6 | % |  | float | Read
42499 | 1 |  | 2 | Status Node6 | 0-255 |  | uint16 | Read
42500 | 2 |  | 4 | Temperature Node6 | oC |  | float | Read
42752 | 1 |  | 2 | %Battery Node7 | 10,30,60,99 |  | uint16 | Read | 0xA700..0xA720
42753 | 2 |  | 4 | Pressure Node7 | % |  | float | Read
42755 | 1 |  | 2 | Status Node7 | 0-255 |  | uint16 | Read
42756 | 2 |  | 4 | Temperature Node7 | oC |  | float | Read
43008 | 1 |  | 2 | %Battery Node8 | 10,30,60,99 |  | uint16 | Read | 0xA800..0xA820
43009 | 2 |  | 4 | Pressure Node8 | % |  | float | Read
43011 | 1 |  | 2 | Status Node8 | 0-255 |  | uint16 | Read
43012 | 2 |  | 4 | Temperature Node8 | oC |  | float | Read
43264 | 1 |  | 2 | %Battery Node9 | 10,30,60,99 |  | uint16 | Read | 0xA900..0xA920
43265 | 2 |  | 4 | Pressure Node9 | % |  | float | Read
43267 | 1 |  | 2 | Status Node9 | 0-255 |  | uint16 | Read
43268 | 2 |  | 4 | Temperature Node9 | oC |  | float | Read
43520 | 1 |  | 2 | %Battery Node10 | 10,30,60,99 |  | uint16 | Read | 0xAA00..0xAA20
43521 | 2 |  | 4 | Pressure Node10 | % |  | float | Read
43523 | 1 |  | 2 | Status Node10 | 0-255 |  | uint16 | Read
43524 | 2 |  | 4 | Temperature Node10 | oC |  | float | Read
45312 | 1 |  | 2 | %Battery Node11 | 10,30,60,99 |  | uint16 | Read | 0xB100..0xB120
45313 | 2 |  | 4 | Pressure Node11 | % |  | float | Read
45315 | 1 |  | 2 | Status Node11 | 0-255 |  | uint16 | Read
45316 | 2 |  | 4 | Temperature Node11 | oC |  | float | Read
45568 | 1 |  | 2 | %Battery Node12 | 10,30,60,99 |  | uint16 | Read | 0xB200..0xB220
45569 | 2 |  | 4 | Pressure Node12 | % |  | float | Read
45571 | 1 |  | 2 | Status Node12 | 0-255 |  | uint16 | Read
45572 | 2 |  | 4 | Temperature Node12 | oC |  | float | Read
45824 | 1 |  | 2 | %Battery Node13 | 10,30,60,99 |  | uint16 | Read | 0xB300..0xB320
45825 | 2 |  | 4 | Pressure Node13 | % |  | float | Read
45827 | 1 |  | 2 | Status Node13 | 0-255 |  | uint16 | Read
45828 | 2 |  | 4 | Temperature Node13 | oC |  | float | Read
46080 | 1 |  | 2 | %Battery Node14 | 10,30,60,99 |  | uint16 | Read | 0xB400..0xB420
46081 | 2 |  | 4 | Pressure Node14 | % |  | float | Read
46083 | 1 |  | 2 | Status Node14 | 0-255 |  | uint16 | Read
46084 | 2 |  | 4 | Temperature Node14 | oC |  | float | Read
46336 | 1 |  | 2 | %Battery Node15 | 10,30,60,99 |  | uint16 | Read | 0xB500..0xB520
46337 | 2 |  | 4 | Pressure Node15 | % |  | float | Read
46339 | 1 |  | 2 | Status Node15 | 0-255 |  | uint16 | Read
46340 | 2 |  | 4 | Temperature Node15 | oC |  | float | Read
46592 | 1 |  | 2 | %Battery Node16 | 10,30,60,99 |  | uint16 | Read | 0xB600..0xB620
46593 | 2 |  | 4 | Pressure Node16 | % |  | float | Read
46595 | 1 |  | 2 | Status Node16 | 0-255 |  | uint16 | Read
46596 | 2 |  | 4 | Temperature Node16 | oC |  | float | Read
46848 | 1 |  | 2 | %Battery Node17 | 10,30,60,99 |  | uint16 | Read | 0xB700..0xB720
46849 | 2 |  | 4 | Pressure Node17 | % |  | float | Read
46851 | 1 |  | 2 | Status Node17 | 0-255 |  | uint16 | Read
46852 | 2 |  | 4 | Temperature Node17 | oC |  | float | Read
47104 | 1 |  | 2 | %Battery Node18 | 10,30,60,99 |  | uint16 | Read | 0xB800..0xB820
47105 | 2 |  | 4 | Pressure Node18 | % |  | float | Read
47107 | 1 |  | 2 | Status Node18 | 0-255 |  | uint16 | Read
47108 | 2 |  | 4 | Temperature Node18 | oC |  | float | Read
47360 | 1 |  | 2 | %Battery Node19 | 10,30,60,99 |  | uint16 | Read | 0xB900..0xB920
47361 | 2 |  | 4 | Pressure Node19 | % |  | float | Read
47363 | 1 |  | 2 | Status Node19 | 0-255 |  | uint16 | Read
47364 | 2 |  | 4 | Temperature Node19 | oC |  | float | Read
47616 | 1 |  | 2 | %Battery Node20 | 10,30,60,99 |  | uint16 | Read | 0xBA00..0xBA20
47617 | 2 |  | 4 | Pressure Node20 | % |  | float | Read
47619 | 1 |  | 2 | Status Node20 | 0-255 |  | uint16 | Read
47620 | 2 |  | 4 | Temperature Node20 | oC |  | float | Read
49408 | 1 |  | 2 | %Battery Node21 | 10,30,60,99 |  | uint16 | Read | 0xC100..0xC120
49409 | 2 |  | 4 | Pressure Node21 | % |  | float | Read
49411 | 1 |  | 2 | Status Node21 | 0-255 |  | uint16 | Read
49412 | 2 |  | 4 | Temperature Node21 | oC |  | float | Read
49664 | 1 |  | 2 | %Battery Node22 | 10,30,60,99 |  | uint16 | Read | 0xC200..0xC220
49665 | 2 |  | 4 | Pressure Node22 | % |  | float | Read
49667 | 1 |  | 2 | Status Node22 | 0-255 |  | uint16 | Read
49668 | 2 |  | 4 | Temperature Node22 | oC |  | float | Read
49920 | 1 |  | 2 | %Battery Node23 | 10,30,60,99 |  | uint16 | Read | 0xC300..0xC320
49921 | 2 |  | 4 | Pressure Node23 | % |  | float | Read
49923 | 1 |  | 2 | Status Node23 | 0-255 |  | uint16 | Read
49924 | 2 |  | 4 | Temperature Node23 | oC |  | float | Read
50176 | 1 |  | 2 | %Battery Node24 | 10,30,60,99 |  | uint16 | Read | 0xC400..0xC420
50177 | 2 |  | 4 | Pressure Node24 | % |  | float | Read
50179 | 1 |  | 2 | Status Node24 | 0-255 |  | uint16 | Read
50180 | 2 |  | 4 | Temperature Node24 | oC |  | float | Read
50432 | 1 |  | 2 | %Battery Node25 | 10,30,60,99 |  | uint16 | Read | 0xC500..0xC520
50433 | 2 |  | 4 | Pressure Node25 | % |  | float | Read
50435 | 1 |  | 2 | Status Node25 | 0-255 |  | uint16 | Read
50436 | 2 |  | 4 | Temperature Node25 | oC |  | float | Read
50688 | 1 |  | 2 | %Battery Node26 | 10,30,60,99 |  | uint16 | Read | 0xC600..0xC620
50689 | 2 |  | 4 | Pressure Node26 | % |  | float | Read
50691 | 1 |  | 2 | Status Node26 | 0-255 |  | uint16 | Read
50692 | 2 |  | 4 | Temperature Node26 | oC |  | float | Read
50944 | 1 |  | 2 | %Battery Node27 | 10,30,60,99 |  | uint16 | Read | 0xC700..0xC720
50945 | 2 |  | 4 | Pressure Node27 | % |  | float | Read
50947 | 1 |  | 2 | Status Node27 | 0-255 |  | uint16 | Read
50948 | 2 |  | 4 | Temperature Node27 | oC |  | float | Read
51200 | 1 |  | 2 | %Battery Node28 | 10,30,60,99 |  | uint16 | Read | 0xC800..0xC820
51201 | 2 |  | 4 | Pressure Node28 | % |  | float | Read
51203 | 1 |  | 2 | Status Node28 | 0-255 |  | uint16 | Read
51204 | 2 |  | 4 | Temperature Node28 | oC |  | float | Read
51456 | 1 |  | 2 | %Battery Node29 | 10,30,60,99 |  | uint16 | Read | 0xC900..0xC920
51457 | 2 |  | 4 | Pressure Node29 | % |  | float | Read
51459 | 1 |  | 2 | Status Node29 | 0-255 |  | uint16 | Read
51460 | 2 |  | 4 | Temperature Node29 | oC |  | float | Read
51712 | 1 |  | 2 | %Battery Node30 | 10,30,60,99 |  | uint16 | Read | 0xCA00..0xCA20
51713 | 2 |  | 4 | Pressure Node30 | % |  | float | Read
51715 | 1 |  | 2 | Status Node30 | 0-255 |  | uint16 | Read
51716 | 2 |  | 4 | Temperature Node30 | oC |  | float | Read
53504 | 1 |  | 2 | %Battery Node31 | 10,30,60,99 |  | uint16 | Read | 0xD100..0xD120
53505 | 2 |  | 4 | Pressure Node31 | % |  | float | Read
53507 | 1 |  | 2 | Status Node31 | 0-255 |  | uint16 | Read
53508 | 2 |  | 4 | Temperature Node31 | oC |  | float | Read
53760 | 1 |  | 2 | %Battery Node32 | 10,30,60,99 |  | uint16 | Read | 0xD200..0xD220
53761 | 2 |  | 4 | Pressure Node32 | % |  | float | Read
53763 | 1 |  | 2 | Status Node32 | 0-255 |  | uint16 | Read
53764 | 2 |  | 4 | Temperature Node32 | oC |  | float | Read
54016 | 1 |  | 2 | %Battery Node33 | 10,30,60,99 |  | uint16 | Read | 0xD300..0xD320
54017 | 2 |  | 4 | Pressure Node33 | % |  | float | Read
54019 | 1 |  | 2 | Status Node33 | 0-255 |  | uint16 | Read
54020 | 2 |  | 4 | Temperature Node33 | oC |  | float | Read
54272 | 1 |  | 2 | %Battery Node34 | 10,30,60,99 |  | uint16 | Read | 0xD400..0xD420
54273 | 2 |  | 4 | Pressure Node34 | % |  | float | Read
54275 | 1 |  | 2 | Status Node34 | 0-255 |  | uint16 | Read
54276 | 2 |  | 4 | Temperature Node34 | oC |  | float | Read
54528 | 1 |  | 2 | %Battery Node35 | 10,30,60,99 |  | uint16 | Read | 0xD500..0xD520
54529 | 2 |  | 4 | Pressure Node35 | % |  | float | Read
54531 | 1 |  | 2 | Status Node35 | 0-255 |  | uint16 | Read
54532 | 2 |  | 4 | Temperature Node35 | oC |  | float | Read
54784 | 1 |  | 2 | %Battery Node36 | 10,30,60,99 |  | uint16 | Read | 0xD600..0xD620
54785 | 2 |  | 4 | Pressure Node36 | % |  | float | Read
54787 | 1 |  | 2 | Status Node36 | 0-255 |  | uint16 | Read
54788 | 2 |  | 4 | Temperature Node36 | oC |  | float | Read
55040 | 1 |  | 2 | %Battery Node37 | 10,30,60,99 |  | uint16 | Read | 0xD700..0xD720
55041 | 2 |  | 4 | Pressure Node37 | % |  | float | Read
55043 | 1 |  | 2 | Status Node37 | 0-255 |  | uint16 | Read
55044 | 2 |  | 4 | Temperature Node37 | oC |  | float | Read
55296 | 1 |  | 2 | %Battery Node38 | 10,30,60,99 |  | uint16 | Read | 0xD800..0xD820
55297 | 2 |  | 4 | Pressure Node38 | % |  | float | Read
55299 | 1 |  | 2 | Status Node38 | 0-255 |  | uint16 | Read
55300 | 2 |  | 4 | Temperature Node38 | oC |  | float | Read
55552 | 1 |  | 2 | %Battery Node39 | 10,30,60,99 |  | uint16 | Read | 0xD900..0xD920
55553 | 2 |  | 4 | Pressure Node39 | % |  | float | Read
55555 | 1 |  | 2 | Status Node39 | 0-255 |  | uint16 | Read
55556 | 2 |  | 4 | Temperature Node39 | oC |  | float | Read
55808 | 1 |  | 2 | %Battery Node40 | 10,30,60,99 |  | uint16 | Read | 0xDA00..0xDA20
55809 | 2 |  | 4 | Pressure Node40 | % |  | float | Read
55811 | 1 |  | 2 | Status Node40 | 0-255 |  | uint16 | Read
55812 | 2 |  | 4 | Temperature Node40 | oC |  | float | Read
256 | 1 | 0 | 2 | modbus address | 1-247 | 1 | uint16 | Read/Write
257 | 1 | 2 | 2 | modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
258 | 1 | 4 | 2 | modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
259 | 9 | 6 | 18 | serial number |  |  | string | Read/Write(PW)
268 | 2 | 24 | 4 | password for setting |  |  | uint32 | Read/Write | Password = 190577
270 | 2 | 28 | 4 | receiver id |  |  | uint32 | Read/Write(PW)
272 | 1 | 32 | 2 | num of node | 0-40 |  | uint16 | Read/Write
273 | 2 | 34 | 4 | node id 1 |  |  | uint32 | Read/Write
275 | 2 | 38 | 4 | node id 2 |  |  | uint32 | Read/Write
277 | 2 | 42 | 4 | node id 3 |  |  | uint32 | Read/Write
279 | 2 | 46 | 4 | node id 4 |  |  | uint32 | Read/Write
281 | 2 | 50 | 4 | node id 5 |  |  | uint32 | Read/Write
283 | 2 | 54 | 4 | node id 6 |  |  | uint32 | Read/Write
285 | 2 | 58 | 4 | node id 7 |  |  | uint32 | Read/Write
287 | 2 | 62 | 4 | node id 8 |  |  | uint32 | Read/Write
289 | 2 | 66 | 4 | node id 9 |  |  | uint32 | Read/Write
291 | 2 | 70 | 4 | node id 10 |  |  | uint32 | Read/Write
293 | 2 | 74 | 4 | node id 11 |  |  | uint32 | Read/Write
295 | 2 | 78 | 4 | node id 12 |  |  | uint32 | Read/Write
297 | 2 | 82 | 4 | node id 13 |  |  | uint32 | Read/Write
299 | 2 | 86 | 4 | node id 14 |  |  | uint32 | Read/Write
301 | 2 | 90 | 4 | node id 15 |  |  | uint32 | Read/Write
303 | 2 | 94 | 4 | node id 16 |  |  | uint32 | Read/Write
305 | 2 | 98 | 4 | node id 17 |  |  | uint32 | Read/Write
307 | 2 | 102 | 4 | node id 18 |  |  | uint32 | Read/Write
309 | 2 | 106 | 4 | node id 19 |  |  | uint32 | Read/Write
311 | 2 | 110 | 4 | node id 20 |  |  | uint32 | Read/Write
313 | 2 | 114 | 4 | node id 21 |  |  | uint32 | Read/Write
315 | 2 | 118 | 4 | node id 22 |  |  | uint32 | Read/Write
317 | 2 | 122 | 4 | node id 23 |  |  | uint32 | Read/Write
319 | 2 | 126 | 4 | node id 24 |  |  | uint32 | Read/Write
321 | 2 | 130 | 4 | node id 25 |  |  | uint32 | Read/Write
323 | 2 | 134 | 4 | node id 26 |  |  | uint32 | Read/Write
325 | 2 | 138 | 4 | node id 27 |  |  | uint32 | Read/Write
327 | 2 | 142 | 4 | node id 28 |  |  | uint32 | Read/Write
329 | 2 | 146 | 4 | node id 29 |  |  | uint32 | Read/Write
331 | 2 | 150 | 4 | node id 30 |  |  | uint32 | Read/Write
333 | 2 | 154 | 4 | node id 31 |  |  | uint32 | Read/Write
335 | 2 | 158 | 4 | node id 32 |  |  | uint32 | Read/Write
337 | 2 | 162 | 4 | node id 33 |  |  | uint32 | Read/Write
339 | 2 | 166 | 4 | node id 34 |  |  | uint32 | Read/Write
341 | 2 | 170 | 4 | node id 35 |  |  | uint32 | Read/Write
343 | 2 | 174 | 4 | node id 36 |  |  | uint32 | Read/Write
345 | 2 | 178 | 4 | node id 37 |  |  | uint32 | Read/Write
347 | 2 | 182 | 4 | node id 38 |  |  | uint32 | Read/Write
349 | 2 | 186 | 4 | node id 39 |  |  | uint32 | Read/Write
351 | 2 | 190 | 4 | node id 40 |  |  | uint32 | Read/Write
353 | 1 | 194 | 2 | cmp time 1 |  | 15 | uint16 | Read/Write | second
354 | 1 | 196 | 2 | cmp time 2 |  | 30 | uint16 | Read/Write | second
355 | 1 | 198 | 2 | cmp time 3 |  | 45 | uint16 | Read/Write | second
356 | 1 | 200 | 2 | cmp time 4 |  | 60 | uint16 | Read/Write | second
357 | 1 | 202 | 2 | cmp time 5 |  | 300 | uint16 | Read/Write | second
358 | 1 | 204 | 2 | cmp time 6 |  | 600 | uint16 | Read/Write | second
359 | 1 | 206 | 2 | cmp time 7 |  | 900 | uint16 | Read/Write | second
360 | 1 | 208 | 2 | cmp time 8 |  | 1800 | uint16 | Read/Write | second
361 | 1 | 210 | 2 | cmp time 9 |  | 3600 | uint16 | Read/Write | second
362 | 37 | 212 | 74 | spare
399 | 1 | 286 | 2 | sync all node | 0-1 |  | uint16 | Read/Write | 1: restart sync
400 | 1 | 288 | 2 | Update_enable_Node1 |  |  | hex | Read/Write | + update enable = 0xB601 = 46593 => update Cycle_wakeup, cycle_healthstatus of node + update enable = 0xB680 = 46720 => update Data_numblock, data_reg, data_numreg of node + update enable = 0xB640 = 46656 => update Offset temp, humidity, pulse width 4 channel of node + update enable = 0xB620 = 46624 => update Delta temp, humidity, counter of node
401 | 1 | 290 | 2 | Cycle_wakeup_Node1 |  |  | uint16 | Read/Write
402 | 1 | 292 | 2 | Cycle_heathsta_Node1 |  |  | uint16 | Read/Write
403 | 1 | 294 | 2 | Data_numblock_Node1 |  |  | uint16 | Read/Write
404 | 1 | 296 | 2 | Data_reg 1_Node1 |  |  | uint16 | Read/Write
405 | 1 | 298 | 2 | Data_numreg 1_Node1 |  |  | uint16 | Read/Write
406 | 1 | 300 | 2 | Data_reg 2_Node1 |  |  | uint16 | Read/Write
407 | 1 | 302 | 2 | Data_numReg 2_Node1 |  |  | uint16 | Read/Write
408 | 1 | 304 | 2 | Data_reg 3_Node1 |  |  | uint16 | Read/Write
409 | 1 | 306 | 2 | Data_numReg 3_Node1 |  |  | uint16 | Read/Write
410 | 2 | 308 | 4 | Delta_Pressure_Node1 |  |  | float | Read/Write
412 | 2 | 312 | 4 | Offset_Pressure_Node1 |  |  | float | Read/Write
414 | 2 | 316 | 4 | Offset_Temp_Node1 |  |  | float | Read/Write
416 | 14 | 320 | 28 | Reserve_regs_Node1 |  |  |  | Read/Write | reserve registers for node 1= 20 regs = 40 bytes
430 | 1 | 348 | 2 | Update_enable_Node2 |  |  | hex | Read/Write
431 | 1 | 350 | 2 | Cycle_wakeup_Node2 |  |  | uint16 | Read/Write
432 | 1 | 352 | 2 | Cycle_heathsta_Node2 |  |  | uint16 | Read/Write
433 | 1 | 354 | 2 | Data_numblock_Node2 |  |  | uint16 | Read/Write
434 | 1 | 356 | 2 | Data_reg 1_Node2 |  |  | uint16 | Read/Write
435 | 1 | 358 | 2 | Data_numreg 1_Node2 |  |  | uint16 | Read/Write
436 | 1 | 360 | 2 | Data_reg 2_Node2 |  |  | uint16 | Read/Write
437 | 1 | 362 | 2 | Data_numReg 2_Node2 |  |  | uint16 | Read/Write
438 | 1 | 364 | 2 | Data_reg 3_Node2 |  |  | uint16 | Read/Write
439 | 1 | 366 | 2 | Data_numReg 3_Node2 |  |  | uint16 | Read/Write
440 | 2 | 368 | 4 | Delta_Pressure_Node2 |  |  | float | Read/Write
442 | 2 | 372 | 4 | Offset_Pressure_Node2 |  |  | float | Read/Write
444 | 2 | 376 | 4 | Offset_Temp_Node2 |  |  | float | Read/Write
446 | 14 | 380 | 28 | Reserve_regs_Node2 |  |  |  | Read/Write
460 | 1 | 408 | 2 | Update_enable_Node3 |  |  | hex | Read/Write
461 | 1 | 410 | 2 | Cycle_wakeup_Node3 |  |  | uint16 | Read/Write
462 | 1 | 412 | 2 | Cycle_heathsta_Node3 |  |  | uint16 | Read/Write
463 | 1 | 414 | 2 | Data_numblock_Node3 |  |  | uint16 | Read/Write
464 | 1 | 416 | 2 | Data_reg 1_Node3 |  |  | uint16 | Read/Write
465 | 1 | 418 | 2 | Data_numreg 1_Node3 |  |  | uint16 | Read/Write
466 | 1 | 420 | 2 | Data_reg 2_Node3 |  |  | uint16 | Read/Write
467 | 1 | 422 | 2 | Data_numReg 2_Node3 |  |  | uint16 | Read/Write
468 | 1 | 424 | 2 | Data_reg 3_Node3 |  |  | uint16 | Read/Write
469 | 1 | 426 | 2 | Data_numReg 3_Node3 |  |  | uint16 | Read/Write
470 | 2 | 428 | 4 | Delta_Pressure_Node3 |  |  | float | Read/Write
472 | 2 | 432 | 4 | Offset_Pressure_Node3 |  |  | float | Read/Write
474 | 2 | 436 | 4 | Offset_Temp_Node3 |  |  | float | Read/Write
476 | 14 | 440 | 28 | Reserve_regs_Node3 |  |  |  | Read/Write
490 | 1 | 468 | 2 | Update_enable_Node4 |  |  | hex | Read/Write
491 | 1 | 470 | 2 | Cycle_wakeup_Node4 |  |  | uint16 | Read/Write
492 | 1 | 472 | 2 | Cycle_heathsta_Node4 |  |  | uint16 | Read/Write
493 | 1 | 474 | 2 | Data_numblock_Node4 |  |  | uint16 | Read/Write
494 | 1 | 476 | 2 | Data_reg 1_Node4 |  |  | uint16 | Read/Write
495 | 1 | 478 | 2 | Data_numreg 1_Node4 |  |  | uint16 | Read/Write
496 | 1 | 480 | 2 | Data_reg 2_Node4 |  |  | uint16 | Read/Write
497 | 1 | 482 | 2 | Data_numReg 2_Node4 |  |  | uint16 | Read/Write
498 | 1 | 484 | 2 | Data_reg 3_Node4 |  |  | uint16 | Read/Write
499 | 1 | 486 | 2 | Data_numReg 3_Node4 |  |  | uint16 | Read/Write
500 | 2 | 488 | 4 | Delta_Pressure_Node4 |  |  | float | Read/Write
502 | 2 | 492 | 4 | Offset_Pressure_Node4 |  |  | float | Read/Write
504 | 2 | 496 | 4 | Offset_Temp_Node4 |  |  | float | Read/Write
506 | 14 | 500 | 28 | Reserve_regs_Node4 |  |  |  | Read/Write
520 | 1 | 528 | 2 | Update_enable_Node5 |  |  | hex | Read/Write
521 | 1 | 530 | 2 | Cycle_wakeup_Node5 |  |  | uint16 | Read/Write
522 | 1 | 532 | 2 | Cycle_heathsta_Node5 |  |  | uint16 | Read/Write
523 | 1 | 534 | 2 | Data_numblock_Node5 |  |  | uint16 | Read/Write
524 | 1 | 536 | 2 | Data_reg 1_Node5 |  |  | uint16 | Read/Write
525 | 1 | 538 | 2 | Data_numreg 1_Node5 |  |  | uint16 | Read/Write
526 | 1 | 540 | 2 | Data_reg 2_Node5 |  |  | uint16 | Read/Write
527 | 1 | 542 | 2 | Data_numReg 2_Node5 |  |  | uint16 | Read/Write
528 | 1 | 544 | 2 | Data_reg 3_Node5 |  |  | uint16 | Read/Write
529 | 1 | 546 | 2 | Data_numReg 3_Node5 |  |  | uint16 | Read/Write
530 | 2 | 548 | 4 | Delta_Pressure_Node5 |  |  | float | Read/Write
532 | 2 | 552 | 4 | Offset_Pressure_Node5 |  |  | float | Read/Write
534 | 2 | 556 | 4 | Offset_Temp_Node5 |  |  | float | Read/Write
536 | 14 | 560 | 28 | Reserve_regs_Node5 |  |  |  | Read/Write
550 | 1 | 588 | 2 | Update_enable_Node6 |  |  | hex | Read/Write
551 | 1 | 590 | 2 | Cycle_wakeup_Node6 |  |  | uint16 | Read/Write
552 | 1 | 592 | 2 | Cycle_heathsta_Node6 |  |  | uint16 | Read/Write
553 | 1 | 594 | 2 | Data_numblock_Node6 |  |  | uint16 | Read/Write
554 | 1 | 596 | 2 | Data_reg 1_Node6 |  |  | uint16 | Read/Write
555 | 1 | 598 | 2 | Data_numreg 1_Node6 |  |  | uint16 | Read/Write
556 | 1 | 600 | 2 | Data_reg 2_Node6 |  |  | uint16 | Read/Write
557 | 1 | 602 | 2 | Data_numReg 2_Node6 |  |  | uint16 | Read/Write
558 | 1 | 604 | 2 | Data_reg 3_Node6 |  |  | uint16 | Read/Write
559 | 1 | 606 | 2 | Data_numReg 3_Node6 |  |  | uint16 | Read/Write
560 | 2 | 608 | 4 | Delta_Pressure_Node6 |  |  | float | Read/Write
562 | 2 | 612 | 4 | Offset_Pressure_Node6 |  |  | float | Read/Write
564 | 2 | 616 | 4 | Offset_Temp_Node6 |  |  | float | Read/Write
566 | 14 | 620 | 28 | Reserve_regs_Node6 |  |  |  | Read/Write
580 | 1 | 648 | 2 | Update_enable_Node7 |  |  | hex | Read/Write
581 | 1 | 650 | 2 | Cycle_wakeup_Node7 |  |  | uint16 | Read/Write
582 | 1 | 652 | 2 | Cycle_heathsta_Node7 |  |  | uint16 | Read/Write
583 | 1 | 654 | 2 | Data_numblock_Node7 |  |  | uint16 | Read/Write
584 | 1 | 656 | 2 | Data_reg 1_Node7 |  |  | uint16 | Read/Write
585 | 1 | 658 | 2 | Data_numreg 1_Node7 |  |  | uint16 | Read/Write
586 | 1 | 660 | 2 | Data_reg 2_Node7 |  |  | uint16 | Read/Write
587 | 1 | 662 | 2 | Data_numReg 2_Node7 |  |  | uint16 | Read/Write
588 | 1 | 664 | 2 | Data_reg 3_Node7 |  |  | uint16 | Read/Write
589 | 1 | 666 | 2 | Data_numReg 3_Node7 |  |  | uint16 | Read/Write
590 | 2 | 668 | 4 | Delta_Pressure_Node7 |  |  | float | Read/Write
592 | 2 | 672 | 4 | Offset_Pressure_Node7 |  |  | float | Read/Write
594 | 2 | 676 | 4 | Offset_Temp_Node7 |  |  | float | Read/Write
596 | 14 | 680 | 28 | Reserve_regs_Node7 |  |  |  | Read/Write
610 | 1 | 708 | 2 | Update_enable_Node8 |  |  | hex | Read/Write
611 | 1 | 710 | 2 | Cycle_wakeup_Node8 |  |  | uint16 | Read/Write
612 | 1 | 712 | 2 | Cycle_heathsta_Node8 |  |  | uint16 | Read/Write
613 | 1 | 714 | 2 | Data_numblock_Node8 |  |  | uint16 | Read/Write
614 | 1 | 716 | 2 | Data_reg 1_Node8 |  |  | uint16 | Read/Write
615 | 1 | 718 | 2 | Data_numreg 1_Node8 |  |  | uint16 | Read/Write
616 | 1 | 720 | 2 | Data_reg 2_Node8 |  |  | uint16 | Read/Write
617 | 1 | 722 | 2 | Data_numReg 2_Node8 |  |  | uint16 | Read/Write
618 | 1 | 724 | 2 | Data_reg 3_Node8 |  |  | uint16 | Read/Write
619 | 1 | 726 | 2 | Data_numReg 3_Node8 |  |  | uint16 | Read/Write
620 | 2 | 728 | 4 | Delta_Pressure_Node8 |  |  | float | Read/Write
622 | 2 | 732 | 4 | Offset_Pressure_Node8 |  |  | float | Read/Write
624 | 2 | 736 | 4 | Offset_Temp_Node8 |  |  | float | Read/Write
626 | 14 | 740 | 28 | Reserve_regs_Node8 |  |  |  | Read/Write
640 | 1 | 768 | 2 | Update_enable_Node9 |  |  | hex | Read/Write
641 | 1 | 770 | 2 | Cycle_wakeup_Node9 |  |  | uint16 | Read/Write
642 | 1 | 772 | 2 | Cycle_heathsta_Node9 |  |  | uint16 | Read/Write
643 | 1 | 774 | 2 | Data_numblock_Node9 |  |  | uint16 | Read/Write
644 | 1 | 776 | 2 | Data_reg 1_Node9 |  |  | uint16 | Read/Write
645 | 1 | 778 | 2 | Data_numreg 1_Node9 |  |  | uint16 | Read/Write
646 | 1 | 780 | 2 | Data_reg 2_Node9 |  |  | uint16 | Read/Write
647 | 1 | 782 | 2 | Data_numReg 2_Node9 |  |  | uint16 | Read/Write
648 | 1 | 784 | 2 | Data_reg 3_Node9 |  |  | uint16 | Read/Write
649 | 1 | 786 | 2 | Data_numReg 3_Node9 |  |  | uint16 | Read/Write
650 | 2 | 788 | 4 | Delta_Pressure_Node9 |  |  | float | Read/Write
652 | 2 | 792 | 4 | Offset_Pressure_Node9 |  |  | float | Read/Write
654 | 2 | 796 | 4 | Offset_Temp_Node9 |  |  | float | Read/Write
656 | 14 | 800 | 28 | Reserve_regs_Node9 |  |  |  | Read/Write
670 | 1 | 828 | 2 | Update_enable_Node10 |  |  | hex | Read/Write
671 | 1 | 830 | 2 | Cycle_wakeup_Node10 |  |  | uint16 | Read/Write
672 | 1 | 832 | 2 | Cycle_heathsta_Node10 |  |  | uint16 | Read/Write
673 | 1 | 834 | 2 | Data_numblock_Node10 |  |  | uint16 | Read/Write
674 | 1 | 836 | 2 | Data_reg 1_Node10 |  |  | uint16 | Read/Write
675 | 1 | 838 | 2 | Data_numreg 1_Node10 |  |  | uint16 | Read/Write
676 | 1 | 840 | 2 | Data_reg 2_Node10 |  |  | uint16 | Read/Write
677 | 1 | 842 | 2 | Data_numReg 2_Node10 |  |  | uint16 | Read/Write
678 | 1 | 844 | 2 | Data_reg 3_Node10 |  |  | uint16 | Read/Write
679 | 1 | 846 | 2 | Data_numReg 3_Node10 |  |  | uint16 | Read/Write
680 | 2 | 848 | 4 | Delta_Pressure_Node10 |  |  | float | Read/Write
682 | 2 | 852 | 4 | Offset_Pressure_Node10 |  |  | float | Read/Write
684 | 2 | 856 | 4 | Offset_Temp_Node10 |  |  | float | Read/Write
686 | 14 | 860 | 28 | Reserve_regs_Node10 |  |  |  | Read/Write
700 | 1 | 888 | 2 | Update_enable_Node11 |  |  | hex | Read/Write
701 | 1 | 890 | 2 | Cycle_wakeup_Node11 |  |  | uint16 | Read/Write
702 | 1 | 892 | 2 | Cycle_heathsta_Node11 |  |  | uint16 | Read/Write
703 | 1 | 894 | 2 | Data_numblock_Node11 |  |  | uint16 | Read/Write
704 | 1 | 896 | 2 | Data_reg 1_Node11 |  |  | uint16 | Read/Write
705 | 1 | 898 | 2 | Data_numreg 1_Node11 |  |  | uint16 | Read/Write
706 | 1 | 900 | 2 | Data_reg 2_Node11 |  |  | uint16 | Read/Write
707 | 1 | 902 | 2 | Data_numReg 2_Node11 |  |  | uint16 | Read/Write
708 | 1 | 904 | 2 | Data_reg 3_Node11 |  |  | uint16 | Read/Write
709 | 1 | 906 | 2 | Data_numReg 3_Node11 |  |  | uint16 | Read/Write
710 | 2 | 908 | 4 | Delta_Pressure_Node11 |  |  | float | Read/Write
712 | 2 | 912 | 4 | Offset_Pressure_Node11 |  |  | float | Read/Write
714 | 2 | 916 | 4 | Offset_Temp_Node11 |  |  | float | Read/Write
716 | 14 | 920 | 28 | Reserve_regs_Node11 |  |  |  | Read/Write
730 | 1 | 948 | 2 | Update_enable_Node12 |  |  | hex | Read/Write
731 | 1 | 950 | 2 | Cycle_wakeup_Node12 |  |  | uint16 | Read/Write
732 | 1 | 952 | 2 | Cycle_heathsta_Node12 |  |  | uint16 | Read/Write
733 | 1 | 954 | 2 | Data_numblock_Node12 |  |  | uint16 | Read/Write
734 | 1 | 956 | 2 | Data_reg 1_Node12 |  |  | uint16 | Read/Write
735 | 1 | 958 | 2 | Data_numreg 1_Node12 |  |  | uint16 | Read/Write
736 | 1 | 960 | 2 | Data_reg 2_Node12 |  |  | uint16 | Read/Write
737 | 1 | 962 | 2 | Data_numReg 2_Node12 |  |  | uint16 | Read/Write
738 | 1 | 964 | 2 | Data_reg 3_Node12 |  |  | uint16 | Read/Write
739 | 1 | 966 | 2 | Data_numReg 3_Node12 |  |  | uint16 | Read/Write
740 | 2 | 968 | 4 | Delta_Pressure_Node12 |  |  | float | Read/Write
742 | 2 | 972 | 4 | Offset_Pressure_Node12 |  |  | float | Read/Write
744 | 2 | 976 | 4 | Offset_Temp_Node12 |  |  | float | Read/Write
746 | 14 | 980 | 28 | Reserve_regs_Node12 |  |  |  | Read/Write
760 | 1 | 1008 | 2 | Update_enable_Node13 |  |  | hex | Read/Write
761 | 1 | 1010 | 2 | Cycle_wakeup_Node13 |  |  | uint16 | Read/Write
762 | 1 | 1012 | 2 | Cycle_heathsta_Node13 |  |  | uint16 | Read/Write
763 | 1 | 1014 | 2 | Data_numblock_Node13 |  |  | uint16 | Read/Write
764 | 1 | 1016 | 2 | Data_reg 1_Node13 |  |  | uint16 | Read/Write
765 | 1 | 1018 | 2 | Data_numreg 1_Node13 |  |  | uint16 | Read/Write
766 | 1 | 1020 | 2 | Data_reg 2_Node13 |  |  | uint16 | Read/Write
767 | 1 | 1022 | 2 | Data_numReg 2_Node13 |  |  | uint16 | Read/Write
768 | 1 | 1024 | 2 | Data_reg 3_Node13 |  |  | uint16 | Read/Write
769 | 1 | 1026 | 2 | Data_numReg 3_Node13 |  |  | uint16 | Read/Write
770 | 2 | 1028 | 4 | Delta_Pressure_Node13 |  |  | float | Read/Write
772 | 2 | 1032 | 4 | Offset_Pressure_Node13 |  |  | float | Read/Write
774 | 2 | 1036 | 4 | Offset_Temp_Node13 |  |  | float | Read/Write
776 | 14 | 1040 | 28 | Reserve_regs_Node13 |  |  |  | Read/Write
790 | 1 | 1068 | 2 | Update_enable_Node14 |  |  | hex | Read/Write
791 | 1 | 1070 | 2 | Cycle_wakeup_Node14 |  |  | uint16 | Read/Write
792 | 1 | 1072 | 2 | Cycle_heathsta_Node14 |  |  | uint16 | Read/Write
793 | 1 | 1074 | 2 | Data_numblock_Node14 |  |  | uint16 | Read/Write
794 | 1 | 1076 | 2 | Data_reg 1_Node14 |  |  | uint16 | Read/Write
795 | 1 | 1078 | 2 | Data_numreg 1_Node14 |  |  | uint16 | Read/Write
796 | 1 | 1080 | 2 | Data_reg 2_Node14 |  |  | uint16 | Read/Write
797 | 1 | 1082 | 2 | Data_numReg 2_Node14 |  |  | uint16 | Read/Write
798 | 1 | 1084 | 2 | Data_reg 3_Node14 |  |  | uint16 | Read/Write
799 | 1 | 1086 | 2 | Data_numReg 3_Node14 |  |  | uint16 | Read/Write
800 | 2 | 1088 | 4 | Delta_Pressure_Node14 |  |  | float | Read/Write
802 | 2 | 1092 | 4 | Offset_Pressure_Node14 |  |  | float | Read/Write
804 | 2 | 1096 | 4 | Offset_Temp_Node14 |  |  | float | Read/Write
806 | 14 | 1100 | 28 | Reserve_regs_Node14 |  |  |  | Read/Write
820 | 1 | 1128 | 2 | Update_enable_Node15 |  |  | hex | Read/Write
821 | 1 | 1130 | 2 | Cycle_wakeup_Node15 |  |  | uint16 | Read/Write
822 | 1 | 1132 | 2 | Cycle_heathsta_Node15 |  |  | uint16 | Read/Write
823 | 1 | 1134 | 2 | Data_numblock_Node15 |  |  | uint16 | Read/Write
824 | 1 | 1136 | 2 | Data_reg 1_Node15 |  |  | uint16 | Read/Write
825 | 1 | 1138 | 2 | Data_numreg 1_Node15 |  |  | uint16 | Read/Write
826 | 1 | 1140 | 2 | Data_reg 2_Node15 |  |  | uint16 | Read/Write
827 | 1 | 1142 | 2 | Data_numReg 2_Node15 |  |  | uint16 | Read/Write
828 | 1 | 1144 | 2 | Data_reg 3_Node15 |  |  | uint16 | Read/Write
829 | 1 | 1146 | 2 | Data_numReg 3_Node15 |  |  | uint16 | Read/Write
830 | 2 | 1148 | 4 | Delta_Pressure_Node15 |  |  | float | Read/Write
832 | 2 | 1152 | 4 | Offset_Pressure_Node15 |  |  | float | Read/Write
834 | 2 | 1156 | 4 | Offset_Temp_Node15 |  |  | float | Read/Write
836 | 14 | 1160 | 28 | Reserve_regs_Node15 |  |  |  | Read/Write
850 | 1 | 1188 | 2 | Update_enable_Node16 |  |  | hex | Read/Write
851 | 1 | 1190 | 2 | Cycle_wakeup_Node16 |  |  | uint16 | Read/Write
852 | 1 | 1192 | 2 | Cycle_heathsta_Node16 |  |  | uint16 | Read/Write
853 | 1 | 1194 | 2 | Data_numblock_Node16 |  |  | uint16 | Read/Write
854 | 1 | 1196 | 2 | Data_reg 1_Node16 |  |  | uint16 | Read/Write
855 | 1 | 1198 | 2 | Data_numreg 1_Node16 |  |  | uint16 | Read/Write
856 | 1 | 1200 | 2 | Data_reg 2_Node16 |  |  | uint16 | Read/Write
857 | 1 | 1202 | 2 | Data_numReg 2_Node16 |  |  | uint16 | Read/Write
858 | 1 | 1204 | 2 | Data_reg 3_Node16 |  |  | uint16 | Read/Write
859 | 1 | 1206 | 2 | Data_numReg 3_Node16 |  |  | uint16 | Read/Write
860 | 2 | 1208 | 4 | Delta_Pressure_Node16 |  |  | float | Read/Write
862 | 2 | 1212 | 4 | Offset_Pressure_Node16 |  |  | float | Read/Write
864 | 2 | 1216 | 4 | Offset_Temp_Node16 |  |  | float | Read/Write
866 | 14 | 1220 | 28 | Reserve_regs_Node16 |  |  |  | Read/Write
880 | 1 | 1248 | 2 | Update_enable_Node17 |  |  | hex | Read/Write
881 | 1 | 1250 | 2 | Cycle_wakeup_Node17 |  |  | uint16 | Read/Write
882 | 1 | 1252 | 2 | Cycle_heathsta_Node17 |  |  | uint16 | Read/Write
883 | 1 | 1254 | 2 | Data_numblock_Node17 |  |  | uint16 | Read/Write
884 | 1 | 1256 | 2 | Data_reg 1_Node17 |  |  | uint16 | Read/Write
885 | 1 | 1258 | 2 | Data_numreg 1_Node17 |  |  | uint16 | Read/Write
886 | 1 | 1260 | 2 | Data_reg 2_Node17 |  |  | uint16 | Read/Write
887 | 1 | 1262 | 2 | Data_numReg 2_Node17 |  |  | uint16 | Read/Write
888 | 1 | 1264 | 2 | Data_reg 3_Node17 |  |  | uint16 | Read/Write
889 | 1 | 1266 | 2 | Data_numReg 3_Node17 |  |  | uint16 | Read/Write
890 | 2 | 1268 | 4 | Delta_Pressure_Node17 |  |  | float | Read/Write
892 | 2 | 1272 | 4 | Offset_Pressure_Node17 |  |  | float | Read/Write
894 | 2 | 1276 | 4 | Offset_Temp_Node17 |  |  | float | Read/Write
896 | 14 | 1280 | 28 | Reserve_regs_Node17 |  |  |  | Read/Write
910 | 1 | 1308 | 2 | Update_enable_Node18 |  |  | hex | Read/Write
911 | 1 | 1310 | 2 | Cycle_wakeup_Node18 |  |  | uint16 | Read/Write
912 | 1 | 1312 | 2 | Cycle_heathsta_Node18 |  |  | uint16 | Read/Write
913 | 1 | 1314 | 2 | Data_numblock_Node18 |  |  | uint16 | Read/Write
914 | 1 | 1316 | 2 | Data_reg 1_Node18 |  |  | uint16 | Read/Write
915 | 1 | 1318 | 2 | Data_numreg 1_Node18 |  |  | uint16 | Read/Write
916 | 1 | 1320 | 2 | Data_reg 2_Node18 |  |  | uint16 | Read/Write
917 | 1 | 1322 | 2 | Data_numReg 2_Node18 |  |  | uint16 | Read/Write
918 | 1 | 1324 | 2 | Data_reg 3_Node18 |  |  | uint16 | Read/Write
919 | 1 | 1326 | 2 | Data_numReg 3_Node18 |  |  | uint16 | Read/Write
920 | 2 | 1328 | 4 | Delta_Pressure_Node18 |  |  | float | Read/Write
922 | 2 | 1332 | 4 | Offset_Pressure_Node18 |  |  | float | Read/Write
924 | 2 | 1336 | 4 | Offset_Temp_Node18 |  |  | float | Read/Write
926 | 14 | 1340 | 28 | Reserve_regs_Node18 |  |  |  | Read/Write
940 | 1 | 1368 | 2 | Update_enable_Node19 |  |  | hex | Read/Write
941 | 1 | 1370 | 2 | Cycle_wakeup_Node19 |  |  | uint16 | Read/Write
942 | 1 | 1372 | 2 | Cycle_heathsta_Node19 |  |  | uint16 | Read/Write
943 | 1 | 1374 | 2 | Data_numblock_Node19 |  |  | uint16 | Read/Write
944 | 1 | 1376 | 2 | Data_reg 1_Node19 |  |  | uint16 | Read/Write
945 | 1 | 1378 | 2 | Data_numreg 1_Node19 |  |  | uint16 | Read/Write
946 | 1 | 1380 | 2 | Data_reg 2_Node19 |  |  | uint16 | Read/Write
947 | 1 | 1382 | 2 | Data_numReg 2_Node19 |  |  | uint16 | Read/Write
948 | 1 | 1384 | 2 | Data_reg 3_Node19 |  |  | uint16 | Read/Write
949 | 1 | 1386 | 2 | Data_numReg 3_Node19 |  |  | uint16 | Read/Write
950 | 2 | 1388 | 4 | Delta_Pressure_Node19 |  |  | float | Read/Write
952 | 2 | 1392 | 4 | Offset_Pressure_Node19 |  |  | float | Read/Write
954 | 2 | 1396 | 4 | Offset_Temp_Node19 |  |  | float | Read/Write
956 | 14 | 1400 | 28 | Reserve_regs_Node19 |  |  |  | Read/Write
970 | 1 | 1428 | 2 | Update_enable_Node20 |  |  | hex | Read/Write
971 | 1 | 1430 | 2 | Cycle_wakeup_Node20 |  |  | uint16 | Read/Write
972 | 1 | 1432 | 2 | Cycle_heathsta_Node20 |  |  | uint16 | Read/Write
973 | 1 | 1434 | 2 | Data_numblock_Node20 |  |  | uint16 | Read/Write
974 | 1 | 1436 | 2 | Data_reg 1_Node20 |  |  | uint16 | Read/Write
975 | 1 | 1438 | 2 | Data_numreg 1_Node20 |  |  | uint16 | Read/Write
976 | 1 | 1440 | 2 | Data_reg 2_Node20 |  |  | uint16 | Read/Write
977 | 1 | 1442 | 2 | Data_numReg 2_Node20 |  |  | uint16 | Read/Write
978 | 1 | 1444 | 2 | Data_reg 3_Node20 |  |  | uint16 | Read/Write
979 | 1 | 1446 | 2 | Data_numReg 3_Node20 |  |  | uint16 | Read/Write
980 | 2 | 1448 | 4 | Delta_Pressure_Node20 |  |  | float | Read/Write
982 | 2 | 1452 | 4 | Offset_Pressure_Node20 |  |  | float | Read/Write
984 | 2 | 1456 | 4 | Offset_Temp_Node20 |  |  | float | Read/Write
986 | 14 | 1460 | 28 | Reserve_regs_Node20 |  |  |  | Read/Write
1000 | 1 | 1488 | 2 | Update_enable_Node21 |  |  | hex | Read/Write
1001 | 1 | 1490 | 2 | Cycle_wakeup_Node21 |  |  | uint16 | Read/Write
1002 | 1 | 1492 | 2 | Cycle_heathsta_Node21 |  |  | uint16 | Read/Write
1003 | 1 | 1494 | 2 | Data_numblock_Node21 |  |  | uint16 | Read/Write
1004 | 1 | 1496 | 2 | Data_reg 1_Node21 |  |  | uint16 | Read/Write
1005 | 1 | 1498 | 2 | Data_numreg 1_Node21 |  |  | uint16 | Read/Write
1006 | 1 | 1500 | 2 | Data_reg 2_Node21 |  |  | uint16 | Read/Write
1007 | 1 | 1502 | 2 | Data_numReg 2_Node21 |  |  | uint16 | Read/Write
1008 | 1 | 1504 | 2 | Data_reg 3_Node21 |  |  | uint16 | Read/Write
1009 | 1 | 1506 | 2 | Data_numReg 3_Node21 |  |  | uint16 | Read/Write
1010 | 2 | 1508 | 4 | Delta_Pressure_Node21 |  |  | float | Read/Write
1012 | 2 | 1512 | 4 | Offset_Pressure_Node21 |  |  | float | Read/Write
1014 | 2 | 1516 | 4 | Offset_Temp_Node21 |  |  | float | Read/Write
1016 | 14 | 1520 | 28 | Reserve_regs_Node21 |  |  |  | Read/Write
1030 | 1 | 1548 | 2 | Update_enable_Node22 |  |  | hex | Read/Write
1031 | 1 | 1550 | 2 | Cycle_wakeup_Node22 |  |  | uint16 | Read/Write
1032 | 1 | 1552 | 2 | Cycle_heathsta_Node22 |  |  | uint16 | Read/Write
1033 | 1 | 1554 | 2 | Data_numblock_Node22 |  |  | uint16 | Read/Write
1034 | 1 | 1556 | 2 | Data_reg 1_Node22 |  |  | uint16 | Read/Write
1035 | 1 | 1558 | 2 | Data_numreg 1_Node22 |  |  | uint16 | Read/Write
1036 | 1 | 1560 | 2 | Data_reg 2_Node22 |  |  | uint16 | Read/Write
1037 | 1 | 1562 | 2 | Data_numReg 2_Node22 |  |  | uint16 | Read/Write
1038 | 1 | 1564 | 2 | Data_reg 3_Node22 |  |  | uint16 | Read/Write
1039 | 1 | 1566 | 2 | Data_numReg 3_Node22 |  |  | uint16 | Read/Write
1040 | 2 | 1568 | 4 | Delta_Pressure_Node22 |  |  | float | Read/Write
1042 | 2 | 1572 | 4 | Offset_Pressure_Node22 |  |  | float | Read/Write
1044 | 2 | 1576 | 4 | Offset_Temp_Node22 |  |  | float | Read/Write
1046 | 14 | 1580 | 28 | Reserve_regs_Node22 |  |  |  | Read/Write
1060 | 1 | 1608 | 2 | Update_enable_Node23 |  |  | hex | Read/Write
1061 | 1 | 1610 | 2 | Cycle_wakeup_Node23 |  |  | uint16 | Read/Write
1062 | 1 | 1612 | 2 | Cycle_heathsta_Node23 |  |  | uint16 | Read/Write
1063 | 1 | 1614 | 2 | Data_numblock_Node23 |  |  | uint16 | Read/Write
1064 | 1 | 1616 | 2 | Data_reg 1_Node23 |  |  | uint16 | Read/Write
1065 | 1 | 1618 | 2 | Data_numreg 1_Node23 |  |  | uint16 | Read/Write
1066 | 1 | 1620 | 2 | Data_reg 2_Node23 |  |  | uint16 | Read/Write
1067 | 1 | 1622 | 2 | Data_numReg 2_Node23 |  |  | uint16 | Read/Write
1068 | 1 | 1624 | 2 | Data_reg 3_Node23 |  |  | uint16 | Read/Write
1069 | 1 | 1626 | 2 | Data_numReg 3_Node23 |  |  | uint16 | Read/Write
1070 | 2 | 1628 | 4 | Delta_Pressure_Node23 |  |  | float | Read/Write
1072 | 2 | 1632 | 4 | Offset_Pressure_Node23 |  |  | float | Read/Write
1074 | 2 | 1636 | 4 | Offset_Temp_Node23 |  |  | float | Read/Write
1076 | 14 | 1640 | 28 | Reserve_regs_Node23 |  |  |  | Read/Write
1090 | 1 | 1668 | 2 | Update_enable_Node24 |  |  | hex | Read/Write
1091 | 1 | 1670 | 2 | Cycle_wakeup_Node24 |  |  | uint16 | Read/Write
1092 | 1 | 1672 | 2 | Cycle_heathsta_Node24 |  |  | uint16 | Read/Write
1093 | 1 | 1674 | 2 | Data_numblock_Node24 |  |  | uint16 | Read/Write
1094 | 1 | 1676 | 2 | Data_reg 1_Node24 |  |  | uint16 | Read/Write
1095 | 1 | 1678 | 2 | Data_numreg 1_Node24 |  |  | uint16 | Read/Write
1096 | 1 | 1680 | 2 | Data_reg 2_Node24 |  |  | uint16 | Read/Write
1097 | 1 | 1682 | 2 | Data_numReg 2_Node24 |  |  | uint16 | Read/Write
1098 | 1 | 1684 | 2 | Data_reg 3_Node24 |  |  | uint16 | Read/Write
1099 | 1 | 1686 | 2 | Data_numReg 3_Node24 |  |  | uint16 | Read/Write
1100 | 2 | 1688 | 4 | Delta_Pressure_Node24 |  |  | float | Read/Write
1102 | 2 | 1692 | 4 | Offset_Pressure_Node24 |  |  | float | Read/Write
1104 | 2 | 1696 | 4 | Offset_Temp_Node24 |  |  | float | Read/Write
1106 | 14 | 1700 | 28 | Reserve_regs_Node24 |  |  |  | Read/Write
1120 | 1 | 1728 | 2 | Update_enable_Node25 |  |  | hex | Read/Write
1121 | 1 | 1730 | 2 | Cycle_wakeup_Node25 |  |  | uint16 | Read/Write
1122 | 1 | 1732 | 2 | Cycle_heathsta_Node25 |  |  | uint16 | Read/Write
1123 | 1 | 1734 | 2 | Data_numblock_Node25 |  |  | uint16 | Read/Write
1124 | 1 | 1736 | 2 | Data_reg 1_Node25 |  |  | uint16 | Read/Write
1125 | 1 | 1738 | 2 | Data_numreg 1_Node25 |  |  | uint16 | Read/Write
1126 | 1 | 1740 | 2 | Data_reg 2_Node25 |  |  | uint16 | Read/Write
1127 | 1 | 1742 | 2 | Data_numReg 2_Node25 |  |  | uint16 | Read/Write
1128 | 1 | 1744 | 2 | Data_reg 3_Node25 |  |  | uint16 | Read/Write
1129 | 1 | 1746 | 2 | Data_numReg 3_Node25 |  |  | uint16 | Read/Write
1130 | 2 | 1748 | 4 | Delta_Pressure_Node25 |  |  | float | Read/Write
1132 | 2 | 1752 | 4 | Offset_Pressure_Node25 |  |  | float | Read/Write
1134 | 2 | 1756 | 4 | Offset_Temp_Node25 |  |  | float | Read/Write
1136 | 14 | 1760 | 28 | Reserve_regs_Node25 |  |  |  | Read/Write
1150 | 1 | 1788 | 2 | Update_enable_Node26 |  |  | hex | Read/Write
1151 | 1 | 1790 | 2 | Cycle_wakeup_Node26 |  |  | uint16 | Read/Write
1152 | 1 | 1792 | 2 | Cycle_heathsta_Node26 |  |  | uint16 | Read/Write
1153 | 1 | 1794 | 2 | Data_numblock_Node26 |  |  | uint16 | Read/Write
1154 | 1 | 1796 | 2 | Data_reg 1_Node26 |  |  | uint16 | Read/Write
1155 | 1 | 1798 | 2 | Data_numreg 1_Node26 |  |  | uint16 | Read/Write
1156 | 1 | 1800 | 2 | Data_reg 2_Node26 |  |  | uint16 | Read/Write
1157 | 1 | 1802 | 2 | Data_numReg 2_Node26 |  |  | uint16 | Read/Write
1158 | 1 | 1804 | 2 | Data_reg 3_Node26 |  |  | uint16 | Read/Write
1159 | 1 | 1806 | 2 | Data_numReg 3_Node26 |  |  | uint16 | Read/Write
1160 | 2 | 1808 | 4 | Delta_Pressure_Node26 |  |  | float | Read/Write
1162 | 2 | 1812 | 4 | Offset_Pressure_Node26 |  |  | float | Read/Write
1164 | 2 | 1816 | 4 | Offset_Temp_Node26 |  |  | float | Read/Write
1166 | 14 | 1820 | 28 | Reserve_regs_Node26 |  |  |  | Read/Write
1180 | 1 | 1848 | 2 | Update_enable_Node27 |  |  | hex | Read/Write
1181 | 1 | 1850 | 2 | Cycle_wakeup_Node27 |  |  | uint16 | Read/Write
1182 | 1 | 1852 | 2 | Cycle_heathsta_Node27 |  |  | uint16 | Read/Write
1183 | 1 | 1854 | 2 | Data_numblock_Node27 |  |  | uint16 | Read/Write
1184 | 1 | 1856 | 2 | Data_reg 1_Node27 |  |  | uint16 | Read/Write
1185 | 1 | 1858 | 2 | Data_numreg 1_Node27 |  |  | uint16 | Read/Write
1186 | 1 | 1860 | 2 | Data_reg 2_Node27 |  |  | uint16 | Read/Write
1187 | 1 | 1862 | 2 | Data_numReg 2_Node27 |  |  | uint16 | Read/Write
1188 | 1 | 1864 | 2 | Data_reg 3_Node27 |  |  | uint16 | Read/Write
1189 | 1 | 1866 | 2 | Data_numReg 3_Node27 |  |  | uint16 | Read/Write
1190 | 2 | 1868 | 4 | Delta_Pressure_Node27 |  |  | float | Read/Write
1192 | 2 | 1872 | 4 | Offset_Pressure_Node27 |  |  | float | Read/Write
1194 | 2 | 1876 | 4 | Offset_Temp_Node27 |  |  | float | Read/Write
1196 | 14 | 1880 | 28 | Reserve_regs_Node27 |  |  |  | Read/Write
1210 | 1 | 1908 | 2 | Update_enable_Node28 |  |  | hex | Read/Write
1211 | 1 | 1910 | 2 | Cycle_wakeup_Node28 |  |  | uint16 | Read/Write
1212 | 1 | 1912 | 2 | Cycle_heathsta_Node28 |  |  | uint16 | Read/Write
1213 | 1 | 1914 | 2 | Data_numblock_Node28 |  |  | uint16 | Read/Write
1214 | 1 | 1916 | 2 | Data_reg 1_Node28 |  |  | uint16 | Read/Write
1215 | 1 | 1918 | 2 | Data_numreg 1_Node28 |  |  | uint16 | Read/Write
1216 | 1 | 1920 | 2 | Data_reg 2_Node28 |  |  | uint16 | Read/Write
1217 | 1 | 1922 | 2 | Data_numReg 2_Node28 |  |  | uint16 | Read/Write
1218 | 1 | 1924 | 2 | Data_reg 3_Node28 |  |  | uint16 | Read/Write
1219 | 1 | 1926 | 2 | Data_numReg 3_Node28 |  |  | uint16 | Read/Write
1220 | 2 | 1928 | 4 | Delta_Pressure_Node28 |  |  | float | Read/Write
1222 | 2 | 1932 | 4 | Offset_Pressure_Node28 |  |  | float | Read/Write
1224 | 2 | 1936 | 4 | Offset_Temp_Node28 |  |  | float | Read/Write
1226 | 14 | 1940 | 28 | Reserve_regs_Node28 |  |  |  | Read/Write
1240 | 1 | 1968 | 2 | Update_enable_Node29 |  |  | hex | Read/Write
1241 | 1 | 1970 | 2 | Cycle_wakeup_Node29 |  |  | uint16 | Read/Write
1242 | 1 | 1972 | 2 | Cycle_heathsta_Node29 |  |  | uint16 | Read/Write
1243 | 1 | 1974 | 2 | Data_numblock_Node29 |  |  | uint16 | Read/Write
1244 | 1 | 1976 | 2 | Data_reg 1_Node29 |  |  | uint16 | Read/Write
1245 | 1 | 1978 | 2 | Data_numreg 1_Node29 |  |  | uint16 | Read/Write
1246 | 1 | 1980 | 2 | Data_reg 2_Node29 |  |  | uint16 | Read/Write
1247 | 1 | 1982 | 2 | Data_numReg 2_Node29 |  |  | uint16 | Read/Write
1248 | 1 | 1984 | 2 | Data_reg 3_Node29 |  |  | uint16 | Read/Write
1249 | 1 | 1986 | 2 | Data_numReg 3_Node29 |  |  | uint16 | Read/Write
1250 | 2 | 1988 | 4 | Delta_Pressure_Node29 |  |  | float | Read/Write
1252 | 2 | 1992 | 4 | Offset_Pressure_Node29 |  |  | float | Read/Write
1254 | 2 | 1996 | 4 | Offset_Temp_Node29 |  |  | float | Read/Write
1256 | 14 | 2000 | 28 | Reserve_regs_Node29 |  |  |  | Read/Write
1270 | 1 | 2028 | 2 | Update_enable_Node30 |  |  | hex | Read/Write
1271 | 1 | 2030 | 2 | Cycle_wakeup_Node30 |  |  | uint16 | Read/Write
1272 | 1 | 2032 | 2 | Cycle_heathsta_Node30 |  |  | uint16 | Read/Write
1273 | 1 | 2034 | 2 | Data_numblock_Node30 |  |  | uint16 | Read/Write
1274 | 1 | 2036 | 2 | Data_reg 1_Node30 |  |  | uint16 | Read/Write
1275 | 1 | 2038 | 2 | Data_numreg 1_Node30 |  |  | uint16 | Read/Write
1276 | 1 | 2040 | 2 | Data_reg 2_Node30 |  |  | uint16 | Read/Write
1277 | 1 | 2042 | 2 | Data_numReg 2_Node30 |  |  | uint16 | Read/Write
1278 | 1 | 2044 | 2 | Data_reg 3_Node30 |  |  | uint16 | Read/Write
1279 | 1 | 2046 | 2 | Data_numReg 3_Node30 |  |  | uint16 | Read/Write
1280 | 2 | 2048 | 4 | Delta_Pressure_Node30 |  |  | float | Read/Write
1282 | 2 | 2052 | 4 | Offset_Pressure_Node30 |  |  | float | Read/Write
1284 | 2 | 2056 | 4 | Offset_Temp_Node30 |  |  | float | Read/Write
1286 | 14 | 2060 | 28 | Reserve_regs_Node30 |  |  |  | Read/Write
1300 | 1 | 2088 | 2 | Update_enable_Node31 |  |  | hex | Read/Write
1301 | 1 | 2090 | 2 | Cycle_wakeup_Node31 |  |  | uint16 | Read/Write
1302 | 1 | 2092 | 2 | Cycle_heathsta_Node31 |  |  | uint16 | Read/Write
1303 | 1 | 2094 | 2 | Data_numblock_Node31 |  |  | uint16 | Read/Write
1304 | 1 | 2096 | 2 | Data_reg 1_Node31 |  |  | uint16 | Read/Write
1305 | 1 | 2098 | 2 | Data_numreg 1_Node31 |  |  | uint16 | Read/Write
1306 | 1 | 2100 | 2 | Data_reg 2_Node31 |  |  | uint16 | Read/Write
1307 | 1 | 2102 | 2 | Data_numReg 2_Node31 |  |  | uint16 | Read/Write
1308 | 1 | 2104 | 2 | Data_reg 3_Node31 |  |  | uint16 | Read/Write
1309 | 1 | 2106 | 2 | Data_numReg 3_Node31 |  |  | uint16 | Read/Write
1310 | 2 | 2108 | 4 | Delta_Pressure_Node31 |  |  | float | Read/Write
1312 | 2 | 2112 | 4 | Offset_Pressure_Node31 |  |  | float | Read/Write
1314 | 2 | 2116 | 4 | Offset_Temp_Node31 |  |  | float | Read/Write
1316 | 14 | 2120 | 28 | Reserve_regs_Node31 |  |  |  | Read/Write
1330 | 1 | 2148 | 2 | Update_enable_Node32 |  |  | hex | Read/Write
1331 | 1 | 2150 | 2 | Cycle_wakeup_Node32 |  |  | uint16 | Read/Write
1332 | 1 | 2152 | 2 | Cycle_heathsta_Node32 |  |  | uint16 | Read/Write
1333 | 1 | 2154 | 2 | Data_numblock_Node32 |  |  | uint16 | Read/Write
1334 | 1 | 2156 | 2 | Data_reg 1_Node32 |  |  | uint16 | Read/Write
1335 | 1 | 2158 | 2 | Data_numreg 1_Node32 |  |  | uint16 | Read/Write
1336 | 1 | 2160 | 2 | Data_reg 2_Node32 |  |  | uint16 | Read/Write
1337 | 1 | 2162 | 2 | Data_numReg 2_Node32 |  |  | uint16 | Read/Write
1338 | 1 | 2164 | 2 | Data_reg 3_Node32 |  |  | uint16 | Read/Write
1339 | 1 | 2166 | 2 | Data_numReg 3_Node32 |  |  | uint16 | Read/Write
1340 | 2 | 2168 | 4 | Delta_Pressure_Node32 |  |  | float | Read/Write
1342 | 2 | 2172 | 4 | Offset_Pressure_Node32 |  |  | float | Read/Write
1344 | 2 | 2176 | 4 | Offset_Temp_Node32 |  |  | float | Read/Write
1346 | 14 | 2180 | 28 | Reserve_regs_Node32 |  |  |  | Read/Write
1360 | 1 | 2208 | 2 | Update_enable_Node33 |  |  | hex | Read/Write
1361 | 1 | 2210 | 2 | Cycle_wakeup_Node33 |  |  | uint16 | Read/Write
1362 | 1 | 2212 | 2 | Cycle_heathsta_Node33 |  |  | uint16 | Read/Write
1363 | 1 | 2214 | 2 | Data_numblock_Node33 |  |  | uint16 | Read/Write
1364 | 1 | 2216 | 2 | Data_reg 1_Node33 |  |  | uint16 | Read/Write
1365 | 1 | 2218 | 2 | Data_numreg 1_Node33 |  |  | uint16 | Read/Write
1366 | 1 | 2220 | 2 | Data_reg 2_Node33 |  |  | uint16 | Read/Write
1367 | 1 | 2222 | 2 | Data_numReg 2_Node33 |  |  | uint16 | Read/Write
1368 | 1 | 2224 | 2 | Data_reg 3_Node33 |  |  | uint16 | Read/Write
1369 | 1 | 2226 | 2 | Data_numReg 3_Node33 |  |  | uint16 | Read/Write
1370 | 2 | 2228 | 4 | Delta_Pressure_Node33 |  |  | float | Read/Write
1372 | 2 | 2232 | 4 | Offset_Pressure_Node33 |  |  | float | Read/Write
1374 | 2 | 2236 | 4 | Offset_Temp_Node33 |  |  | float | Read/Write
1376 | 14 | 2240 | 28 | Reserve_regs_Node33 |  |  |  | Read/Write
1390 | 1 | 2268 | 2 | Update_enable_Node34 |  |  | hex | Read/Write
1391 | 1 | 2270 | 2 | Cycle_wakeup_Node34 |  |  | uint16 | Read/Write
1392 | 1 | 2272 | 2 | Cycle_heathsta_Node34 |  |  | uint16 | Read/Write
1393 | 1 | 2274 | 2 | Data_numblock_Node34 |  |  | uint16 | Read/Write
1394 | 1 | 2276 | 2 | Data_reg 1_Node34 |  |  | uint16 | Read/Write
1395 | 1 | 2278 | 2 | Data_numreg 1_Node34 |  |  | uint16 | Read/Write
1396 | 1 | 2280 | 2 | Data_reg 2_Node34 |  |  | uint16 | Read/Write
1397 | 1 | 2282 | 2 | Data_numReg 2_Node34 |  |  | uint16 | Read/Write
1398 | 1 | 2284 | 2 | Data_reg 3_Node34 |  |  | uint16 | Read/Write
1399 | 1 | 2286 | 2 | Data_numReg 3_Node34 |  |  | uint16 | Read/Write
1400 | 2 | 2288 | 4 | Delta_Pressure_Node34 |  |  | float | Read/Write
1402 | 2 | 2292 | 4 | Offset_Pressure_Node34 |  |  | float | Read/Write
1404 | 2 | 2296 | 4 | Offset_Temp_Node34 |  |  | float | Read/Write
1406 | 14 | 2300 | 28 | Reserve_regs_Node34 |  |  |  | Read/Write
1420 | 1 | 2328 | 2 | Update_enable_Node35 |  |  | hex | Read/Write
1421 | 1 | 2330 | 2 | Cycle_wakeup_Node35 |  |  | uint16 | Read/Write
1422 | 1 | 2332 | 2 | Cycle_heathsta_Node35 |  |  | uint16 | Read/Write
1423 | 1 | 2334 | 2 | Data_numblock_Node35 |  |  | uint16 | Read/Write
1424 | 1 | 2336 | 2 | Data_reg 1_Node35 |  |  | uint16 | Read/Write
1425 | 1 | 2338 | 2 | Data_numreg 1_Node35 |  |  | uint16 | Read/Write
1426 | 1 | 2340 | 2 | Data_reg 2_Node35 |  |  | uint16 | Read/Write
1427 | 1 | 2342 | 2 | Data_numReg 2_Node35 |  |  | uint16 | Read/Write
1428 | 1 | 2344 | 2 | Data_reg 3_Node35 |  |  | uint16 | Read/Write
1429 | 1 | 2346 | 2 | Data_numReg 3_Node35 |  |  | uint16 | Read/Write
1430 | 2 | 2348 | 4 | Delta_Pressure_Node35 |  |  | float | Read/Write
1432 | 2 | 2352 | 4 | Offset_Pressure_Node35 |  |  | float | Read/Write
1434 | 2 | 2356 | 4 | Offset_Temp_Node35 |  |  | float | Read/Write
1436 | 14 | 2360 | 28 | Reserve_regs_Node35 |  |  |  | Read/Write
1450 | 1 | 2388 | 2 | Update_enable_Node36 |  |  | hex | Read/Write
1451 | 1 | 2390 | 2 | Cycle_wakeup_Node36 |  |  | uint16 | Read/Write
1452 | 1 | 2392 | 2 | Cycle_heathsta_Node36 |  |  | uint16 | Read/Write
1453 | 1 | 2394 | 2 | Data_numblock_Node36 |  |  | uint16 | Read/Write
1454 | 1 | 2396 | 2 | Data_reg 1_Node36 |  |  | uint16 | Read/Write
1455 | 1 | 2398 | 2 | Data_numreg 1_Node36 |  |  | uint16 | Read/Write
1456 | 1 | 2400 | 2 | Data_reg 2_Node36 |  |  | uint16 | Read/Write
1457 | 1 | 2402 | 2 | Data_numReg 2_Node36 |  |  | uint16 | Read/Write
1458 | 1 | 2404 | 2 | Data_reg 3_Node36 |  |  | uint16 | Read/Write
1459 | 1 | 2406 | 2 | Data_numReg 3_Node36 |  |  | uint16 | Read/Write
1460 | 2 | 2408 | 4 | Delta_Pressure_Node36 |  |  | float | Read/Write
1462 | 2 | 2412 | 4 | Offset_Pressure_Node36 |  |  | float | Read/Write
1464 | 2 | 2416 | 4 | Offset_Temp_Node36 |  |  | float | Read/Write
1466 | 14 | 2420 | 28 | Reserve_regs_Node36 |  |  |  | Read/Write
1480 | 1 | 2448 | 2 | Update_enable_Node37 |  |  | hex | Read/Write
1481 | 1 | 2450 | 2 | Cycle_wakeup_Node37 |  |  | uint16 | Read/Write
1482 | 1 | 2452 | 2 | Cycle_heathsta_Node37 |  |  | uint16 | Read/Write
1483 | 1 | 2454 | 2 | Data_numblock_Node37 |  |  | uint16 | Read/Write
1484 | 1 | 2456 | 2 | Data_reg 1_Node37 |  |  | uint16 | Read/Write
1485 | 1 | 2458 | 2 | Data_numreg 1_Node37 |  |  | uint16 | Read/Write
1486 | 1 | 2460 | 2 | Data_reg 2_Node37 |  |  | uint16 | Read/Write
1487 | 1 | 2462 | 2 | Data_numReg 2_Node37 |  |  | uint16 | Read/Write
1488 | 1 | 2464 | 2 | Data_reg 3_Node37 |  |  | uint16 | Read/Write
1489 | 1 | 2466 | 2 | Data_numReg 3_Node37 |  |  | uint16 | Read/Write
1490 | 2 | 2468 | 4 | Delta_Pressure_Node37 |  |  | float | Read/Write
1492 | 2 | 2472 | 4 | Offset_Pressure_Node37 |  |  | float | Read/Write
1494 | 2 | 2476 | 4 | Offset_Temp_Node37 |  |  | float | Read/Write
1496 | 14 | 2480 | 28 | Reserve_regs_Node37 |  |  |  | Read/Write
1510 | 1 | 2508 | 2 | Update_enable_Node38 |  |  | hex | Read/Write
1511 | 1 | 2510 | 2 | Cycle_wakeup_Node38 |  |  | uint16 | Read/Write
1512 | 1 | 2512 | 2 | Cycle_heathsta_Node38 |  |  | uint16 | Read/Write
1513 | 1 | 2514 | 2 | Data_numblock_Node38 |  |  | uint16 | Read/Write
1514 | 1 | 2516 | 2 | Data_reg 1_Node38 |  |  | uint16 | Read/Write
1515 | 1 | 2518 | 2 | Data_numreg 1_Node38 |  |  | uint16 | Read/Write
1516 | 1 | 2520 | 2 | Data_reg 2_Node38 |  |  | uint16 | Read/Write
1517 | 1 | 2522 | 2 | Data_numReg 2_Node38 |  |  | uint16 | Read/Write
1518 | 1 | 2524 | 2 | Data_reg 3_Node38 |  |  | uint16 | Read/Write
1519 | 1 | 2526 | 2 | Data_numReg 3_Node38 |  |  | uint16 | Read/Write
1520 | 2 | 2528 | 4 | Delta_Pressure_Node38 |  |  | float | Read/Write
1522 | 2 | 2532 | 4 | Offset_Pressure_Node38 |  |  | float | Read/Write
1524 | 2 | 2536 | 4 | Offset_Temp_Node38 |  |  | float | Read/Write
1526 | 14 | 2540 | 28 | Reserve_regs_Node38 |  |  |  | Read/Write
1540 | 1 | 2568 | 2 | Update_enable_Node39 |  |  | hex | Read/Write
1541 | 1 | 2570 | 2 | Cycle_wakeup_Node39 |  |  | uint16 | Read/Write
1542 | 1 | 2572 | 2 | Cycle_heathsta_Node39 |  |  | uint16 | Read/Write
1543 | 1 | 2574 | 2 | Data_numblock_Node39 |  |  | uint16 | Read/Write
1544 | 1 | 2576 | 2 | Data_reg 1_Node39 |  |  | uint16 | Read/Write
1545 | 1 | 2578 | 2 | Data_numreg 1_Node39 |  |  | uint16 | Read/Write
1546 | 1 | 2580 | 2 | Data_reg 2_Node39 |  |  | uint16 | Read/Write
1547 | 1 | 2582 | 2 | Data_numReg 2_Node39 |  |  | uint16 | Read/Write
1548 | 1 | 2584 | 2 | Data_reg 3_Node39 |  |  | uint16 | Read/Write
1549 | 1 | 2586 | 2 | Data_numReg 3_Node39 |  |  | uint16 | Read/Write
1550 | 2 | 2588 | 4 | Delta_Pressure_Node39 |  |  | float | Read/Write
1552 | 2 | 2592 | 4 | Offset_Pressure_Node39 |  |  | float | Read/Write
1554 | 2 | 2596 | 4 | Offset_Temp_Node39 |  |  | float | Read/Write
1556 | 14 | 2600 | 28 | Reserve_regs_Node39 |  |  |  | Read/Write
1570 | 1 | 2628 | 2 | Update_enable_Node40 |  |  | hex | Read/Write
1571 | 1 | 2630 | 2 | Cycle_wakeup_Node40 |  |  | uint16 | Read/Write
1572 | 1 | 2632 | 2 | Cycle_heathsta_Node40 |  |  | uint16 | Read/Write
1573 | 1 | 2634 | 2 | Data_numblock_Node40 |  |  | uint16 | Read/Write
1574 | 1 | 2636 | 2 | Data_reg 1_Node40 |  |  | uint16 | Read/Write
1575 | 1 | 2638 | 2 | Data_numreg 1_Node40 |  |  | uint16 | Read/Write
1576 | 1 | 2640 | 2 | Data_reg 2_Node40 |  |  | uint16 | Read/Write
1577 | 1 | 2642 | 2 | Data_numReg 2_Node40 |  |  | uint16 | Read/Write
1578 | 1 | 2644 | 2 | Data_reg 3_Node40 |  |  | uint16 | Read/Write
1579 | 1 | 2646 | 2 | Data_numReg 3_Node40 |  |  | uint16 | Read/Write
1580 | 2 | 2648 | 4 | Delta_Pressure_Node40 |  |  | float | Read/Write
1582 | 2 | 2652 | 4 | Offset_Pressure_Node40 |  |  | float | Read/Write
1584 | 2 | 2656 | 4 | Offset_Temp_Node40 |  |  | float | Read/Write
1586 | 14 | 2660 | 28 | Reserve_regs_Node40 |  |  |  | Read/Write

## Sensor là Differential Pressure (hidden)
Modbus Register | # of register | Adr | Size | Description | Range | Default | Format | Property | Comment
41216 | 1 |  | 2 | %Battery Node1 | 10,30,60,99 |  | uint16 | Read | Wireless Sensor là loại cảm biến chênh áp, 0xA100..0xA120
41217 | 2 |  | 4 | Differential Pressure Node1 | -125..+125Pa |  | float | Read | Diff.pressure output = -125..+125 Pa
41219 | 1 |  | 2 | Status Node1 | 0-255 |  | uint16 | Read | Byte Hi "error", byte lo "loại sensor": + byte lo = 1: cảm biến nhiệt độ + byte lo = 2: cảm biến độ ẩm + byte lo = 3: cảm biến chênh áp môi trường + byte lo = 4: cảm biến áp suất + byte lo = 5: cảm biến 1 kênh đo dòng AC + byte lo = 6: cảm biến digital input, 2 kênh Counter + byte lo = 7: cảm biến digital input, 2 kênh Status + byte lo = 8: cảm biến 2 kênh volts 3vdc + byte lo = 9: cảm biến 1 kênh 0-20mA + byte lo = 10: cảm biến ngõ ra 4 kênh relay SPST + byte lo = 11: cảm biến ngõ ra 2 kênh relay SPDT + byte lo = 12: cảm biến ánh sáng môi trường + byte lo = 255: không có cảm biến + byte hi = 0: không có lỗi + byte hi = 1: đã thay đổi loại sensor port M12F mà chưa reset để nhận dạng cảm biến mới + byte hi = 2: sensor port M12F chạm GND + byte hi = 3: sensor port M12F chạm Vcc + byte hi = 4: sensor port M12F chạm nhau + byte hi = 51: sensor port uart bị lỗi check sum
41220 | 2 |  | 4 | Temperature Node1 | oC |  | float | Read
41472 | 1 |  | 2 | %Battery Node2 | 10,30,60,99 |  | uint16 | Read | 0xA200..0xA220
41473 | 2 |  | 4 | Differential Pressure Node2 | -125..+125Pa |  | float | Read
41475 | 1 |  | 2 | Status Node2 | 0-255 |  | uint16 | Read
41476 | 2 |  | 4 | Temperature Node2 | oC |  | float | Read
41728 | 1 |  | 2 | %Battery Node3 | 10,30,60,99 |  | uint16 | Read | 0xA300..0xA320
41729 | 2 |  | 4 | Differential Pressure Node3 | -125..+125Pa |  | float | Read
41731 | 1 |  | 2 | Status Node3 | 0-255 |  | uint16 | Read
41732 | 2 |  | 4 | Temperature Node3 | oC |  | float | Read
41984 | 1 |  | 2 | %Battery Node4 | 10,30,60,99 |  | uint16 | Read | 0xA400..0xA420
41985 | 2 |  | 4 | Differential Pressure Node4 | -125..+125Pa |  | float | Read
41987 | 1 |  | 2 | Status Node4 | 0-255 |  | uint16 | Read
41988 | 2 |  | 4 | Temperature Node4 | oC |  | float | Read
42240 | 1 |  | 2 | %Battery Node5 | 10,30,60,99 |  | uint16 | Read | 0xA500..0xA520
42241 | 2 |  | 4 | Differential Pressure Node5 | -125..+125Pa |  | float | Read
42243 | 1 |  | 2 | Status Node5 | 0-255 |  | uint16 | Read
42244 | 2 |  | 4 | Temperature Node5 | oC |  | float | Read
42496 | 1 |  | 2 | %Battery Node6 | 10,30,60,99 |  | uint16 | Read | 0xA600..0xA620
42497 | 2 |  | 4 | Differential Pressure Node6 | -125..+125Pa |  | float | Read
42499 | 1 |  | 2 | Status Node6 | 0-255 |  | uint16 | Read
42500 | 2 |  | 4 | Temperature Node6 | oC |  | float | Read
42752 | 1 |  | 2 | %Battery Node7 | 10,30,60,99 |  | uint16 | Read | 0xA700..0xA720
42753 | 2 |  | 4 | Differential Pressure Node7 | -125..+125Pa |  | float | Read
42755 | 1 |  | 2 | Status Node7 | 0-255 |  | uint16 | Read
42756 | 2 |  | 4 | Temperature Node7 | oC |  | float | Read
43008 | 1 |  | 2 | %Battery Node8 | 10,30,60,99 |  | uint16 | Read | 0xA800..0xA820
43009 | 2 |  | 4 | Differential Pressure Node8 | -125..+125Pa |  | float | Read
43011 | 1 |  | 2 | Status Node8 | 0-255 |  | uint16 | Read
43012 | 2 |  | 4 | Temperature Node8 | oC |  | float | Read
43264 | 1 |  | 2 | %Battery Node9 | 10,30,60,99 |  | uint16 | Read | 0xA900..0xA920
43265 | 2 |  | 4 | Differential Pressure Node9 | -125..+125Pa |  | float | Read
43267 | 1 |  | 2 | Status Node9 | 0-255 |  | uint16 | Read
43268 | 2 |  | 4 | Temperature Node9 | oC |  | float | Read
43520 | 1 |  | 2 | %Battery Node10 | 10,30,60,99 |  | uint16 | Read | 0xAA00..0xAA20
43521 | 2 |  | 4 | Differential Pressure Node10 | -125..+125Pa |  | float | Read
43523 | 1 |  | 2 | Status Node10 | 0-255 |  | uint16 | Read
43524 | 2 |  | 4 | Temperature Node10 | oC |  | float | Read
45312 | 1 |  | 2 | %Battery Node11 | 10,30,60,99 |  | uint16 | Read | 0xB100..0xB120
45313 | 2 |  | 4 | Differential Pressure Node11 | -125..+125Pa |  | float | Read
45315 | 1 |  | 2 | Status Node11 | 0-255 |  | uint16 | Read
45316 | 2 |  | 4 | Temperature Node11 | oC |  | float | Read
45568 | 1 |  | 2 | %Battery Node12 | 10,30,60,99 |  | uint16 | Read | 0xB200..0xB220
45569 | 2 |  | 4 | Differential Pressure Node12 | -125..+125Pa |  | float | Read
45571 | 1 |  | 2 | Status Node12 | 0-255 |  | uint16 | Read
45572 | 2 |  | 4 | Temperature Node12 | oC |  | float | Read
45824 | 1 |  | 2 | %Battery Node13 | 10,30,60,99 |  | uint16 | Read | 0xB300..0xB320
45825 | 2 |  | 4 | Differential Pressure Node13 | -125..+125Pa |  | float | Read
45827 | 1 |  | 2 | Status Node13 | 0-255 |  | uint16 | Read
45828 | 2 |  | 4 | Temperature Node13 | oC |  | float | Read
46080 | 1 |  | 2 | %Battery Node14 | 10,30,60,99 |  | uint16 | Read | 0xB400..0xB420
46081 | 2 |  | 4 | Differential Pressure Node14 | -125..+125Pa |  | float | Read
46083 | 1 |  | 2 | Status Node14 | 0-255 |  | uint16 | Read
46084 | 2 |  | 4 | Temperature Node14 | oC |  | float | Read
46336 | 1 |  | 2 | %Battery Node15 | 10,30,60,99 |  | uint16 | Read | 0xB500..0xB520
46337 | 2 |  | 4 | Differential Pressure Node15 | -125..+125Pa |  | float | Read
46339 | 1 |  | 2 | Status Node15 | 0-255 |  | uint16 | Read
46340 | 2 |  | 4 | Temperature Node15 | oC |  | float | Read
46592 | 1 |  | 2 | %Battery Node16 | 10,30,60,99 |  | uint16 | Read | 0xB600..0xB620
46593 | 2 |  | 4 | Differential Pressure Node16 | -125..+125Pa |  | float | Read
46595 | 1 |  | 2 | Status Node16 | 0-255 |  | uint16 | Read
46596 | 2 |  | 4 | Temperature Node16 | oC |  | float | Read
46848 | 1 |  | 2 | %Battery Node17 | 10,30,60,99 |  | uint16 | Read | 0xB700..0xB720
46849 | 2 |  | 4 | Differential Pressure Node17 | -125..+125Pa |  | float | Read
46851 | 1 |  | 2 | Status Node17 | 0-255 |  | uint16 | Read
46852 | 2 |  | 4 | Temperature Node17 | oC |  | float | Read
47104 | 1 |  | 2 | %Battery Node18 | 10,30,60,99 |  | uint16 | Read | 0xB800..0xB820
47105 | 2 |  | 4 | Differential Pressure Node18 | -125..+125Pa |  | float | Read
47107 | 1 |  | 2 | Status Node18 | 0-255 |  | uint16 | Read
47108 | 2 |  | 4 | Temperature Node18 | oC |  | float | Read
47360 | 1 |  | 2 | %Battery Node19 | 10,30,60,99 |  | uint16 | Read | 0xB900..0xB920
47361 | 2 |  | 4 | Differential Pressure Node19 | -125..+125Pa |  | float | Read
47363 | 1 |  | 2 | Status Node19 | 0-255 |  | uint16 | Read
47364 | 2 |  | 4 | Temperature Node19 | oC |  | float | Read
47616 | 1 |  | 2 | %Battery Node20 | 10,30,60,99 |  | uint16 | Read | 0xBA00..0xBA20
47617 | 2 |  | 4 | Differential Pressure Node20 | -125..+125Pa |  | float | Read
47619 | 1 |  | 2 | Status Node20 | 0-255 |  | uint16 | Read
47620 | 2 |  | 4 | Temperature Node20 | oC |  | float | Read
49408 | 1 |  | 2 | %Battery Node21 | 10,30,60,99 |  | uint16 | Read | 0xC100..0xC120
49409 | 2 |  | 4 | Differential Pressure Node21 | -125..+125Pa |  | float | Read
49411 | 1 |  | 2 | Status Node21 | 0-255 |  | uint16 | Read
49412 | 2 |  | 4 | Temperature Node21 | oC |  | float | Read
49664 | 1 |  | 2 | %Battery Node22 | 10,30,60,99 |  | uint16 | Read | 0xC200..0xC220
49665 | 2 |  | 4 | Differential Pressure Node22 | -125..+125Pa |  | float | Read
49667 | 1 |  | 2 | Status Node22 | 0-255 |  | uint16 | Read
49668 | 2 |  | 4 | Temperature Node22 | oC |  | float | Read
49920 | 1 |  | 2 | %Battery Node23 | 10,30,60,99 |  | uint16 | Read | 0xC300..0xC320
49921 | 2 |  | 4 | Differential Pressure Node23 | -125..+125Pa |  | float | Read
49923 | 1 |  | 2 | Status Node23 | 0-255 |  | uint16 | Read
49924 | 2 |  | 4 | Temperature Node23 | oC |  | float | Read
50176 | 1 |  | 2 | %Battery Node24 | 10,30,60,99 |  | uint16 | Read | 0xC400..0xC420
50177 | 2 |  | 4 | Differential Pressure Node24 | -125..+125Pa |  | float | Read
50179 | 1 |  | 2 | Status Node24 | 0-255 |  | uint16 | Read
50180 | 2 |  | 4 | Temperature Node24 | oC |  | float | Read
50432 | 1 |  | 2 | %Battery Node25 | 10,30,60,99 |  | uint16 | Read | 0xC500..0xC520
50433 | 2 |  | 4 | Differential Pressure Node25 | -125..+125Pa |  | float | Read
50435 | 1 |  | 2 | Status Node25 | 0-255 |  | uint16 | Read
50436 | 2 |  | 4 | Temperature Node25 | oC |  | float | Read
50688 | 1 |  | 2 | %Battery Node26 | 10,30,60,99 |  | uint16 | Read | 0xC600..0xC620
50689 | 2 |  | 4 | Differential Pressure Node26 | -125..+125Pa |  | float | Read
50691 | 1 |  | 2 | Status Node26 | 0-255 |  | uint16 | Read
50692 | 2 |  | 4 | Temperature Node26 | oC |  | float | Read
50944 | 1 |  | 2 | %Battery Node27 | 10,30,60,99 |  | uint16 | Read | 0xC700..0xC720
50945 | 2 |  | 4 | Differential Pressure Node27 | -125..+125Pa |  | float | Read
50947 | 1 |  | 2 | Status Node27 | 0-255 |  | uint16 | Read
50948 | 2 |  | 4 | Temperature Node27 | oC |  | float | Read
51200 | 1 |  | 2 | %Battery Node28 | 10,30,60,99 |  | uint16 | Read | 0xC800..0xC820
51201 | 2 |  | 4 | Differential Pressure Node28 | -125..+125Pa |  | float | Read
51203 | 1 |  | 2 | Status Node28 | 0-255 |  | uint16 | Read
51204 | 2 |  | 4 | Temperature Node28 | oC |  | float | Read
51456 | 1 |  | 2 | %Battery Node29 | 10,30,60,99 |  | uint16 | Read | 0xC900..0xC920
51457 | 2 |  | 4 | Differential Pressure Node29 | -125..+125Pa |  | float | Read
51459 | 1 |  | 2 | Status Node29 | 0-255 |  | uint16 | Read
51460 | 2 |  | 4 | Temperature Node29 | oC |  | float | Read
51712 | 1 |  | 2 | %Battery Node30 | 10,30,60,99 |  | uint16 | Read | 0xCA00..0xCA20
51713 | 2 |  | 4 | Differential Pressure Node30 | -125..+125Pa |  | float | Read
51715 | 1 |  | 2 | Status Node30 | 0-255 |  | uint16 | Read
51716 | 2 |  | 4 | Temperature Node30 | oC |  | float | Read
53504 | 1 |  | 2 | %Battery Node31 | 10,30,60,99 |  | uint16 | Read | 0xD100..0xD120
53505 | 2 |  | 4 | Differential Pressure Node31 | -125..+125Pa |  | float | Read
53507 | 1 |  | 2 | Status Node31 | 0-255 |  | uint16 | Read
53508 | 2 |  | 4 | Temperature Node31 | oC |  | float | Read
53760 | 1 |  | 2 | %Battery Node32 | 10,30,60,99 |  | uint16 | Read | 0xD200..0xD220
53761 | 2 |  | 4 | Differential Pressure Node32 | -125..+125Pa |  | float | Read
53763 | 1 |  | 2 | Status Node32 | 0-255 |  | uint16 | Read
53764 | 2 |  | 4 | Temperature Node32 | oC |  | float | Read
54016 | 1 |  | 2 | %Battery Node33 | 10,30,60,99 |  | uint16 | Read | 0xD300..0xD320
54017 | 2 |  | 4 | Differential Pressure Node33 | -125..+125Pa |  | float | Read
54019 | 1 |  | 2 | Status Node33 | 0-255 |  | uint16 | Read
54020 | 2 |  | 4 | Temperature Node33 | oC |  | float | Read
54272 | 1 |  | 2 | %Battery Node34 | 10,30,60,99 |  | uint16 | Read | 0xD400..0xD420
54273 | 2 |  | 4 | Differential Pressure Node34 | -125..+125Pa |  | float | Read
54275 | 1 |  | 2 | Status Node34 | 0-255 |  | uint16 | Read
54276 | 2 |  | 4 | Temperature Node34 | oC |  | float | Read
54528 | 1 |  | 2 | %Battery Node35 | 10,30,60,99 |  | uint16 | Read | 0xD500..0xD520
54529 | 2 |  | 4 | Differential Pressure Node35 | -125..+125Pa |  | float | Read
54531 | 1 |  | 2 | Status Node35 | 0-255 |  | uint16 | Read
54532 | 2 |  | 4 | Temperature Node35 | oC |  | float | Read
54784 | 1 |  | 2 | %Battery Node36 | 10,30,60,99 |  | uint16 | Read | 0xD600..0xD620
54785 | 2 |  | 4 | Differential Pressure Node36 | -125..+125Pa |  | float | Read
54787 | 1 |  | 2 | Status Node36 | 0-255 |  | uint16 | Read
54788 | 2 |  | 4 | Temperature Node36 | oC |  | float | Read
55040 | 1 |  | 2 | %Battery Node37 | 10,30,60,99 |  | uint16 | Read | 0xD700..0xD720
55041 | 2 |  | 4 | Differential Pressure Node37 | -125..+125Pa |  | float | Read
55043 | 1 |  | 2 | Status Node37 | 0-255 |  | uint16 | Read
55044 | 2 |  | 4 | Temperature Node37 | oC |  | float | Read
55296 | 1 |  | 2 | %Battery Node38 | 10,30,60,99 |  | uint16 | Read | 0xD800..0xD820
55297 | 2 |  | 4 | Differential Pressure Node38 | -125..+125Pa |  | float | Read
55299 | 1 |  | 2 | Status Node38 | 0-255 |  | uint16 | Read
55300 | 2 |  | 4 | Temperature Node38 | oC |  | float | Read
55552 | 1 |  | 2 | %Battery Node39 | 10,30,60,99 |  | uint16 | Read | 0xD900..0xD920
55553 | 2 |  | 4 | Differential Pressure Node39 | -125..+125Pa |  | float | Read
55555 | 1 |  | 2 | Status Node39 | 0-255 |  | uint16 | Read
55556 | 2 |  | 4 | Temperature Node39 | oC |  | float | Read
55808 | 1 |  | 2 | %Battery Node40 | 10,30,60,99 |  | uint16 | Read | 0xDA00..0xDA20
55809 | 2 |  | 4 | Differential Pressure Node40 | -125..+125Pa |  | float | Read
55811 | 1 |  | 2 | Status Node40 | 0-255 |  | uint16 | Read
55812 | 2 |  | 4 | Temperature Node40 | oC |  | float | Read
256 | 1 | 0 | 2 | modbus address | 1-247 | 1 | uint16 | Read/Write
257 | 1 | 2 | 2 | modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
258 | 1 | 4 | 2 | modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
259 | 9 | 6 | 18 | serial number |  |  | string | Read/Write(PW)
268 | 2 | 24 | 4 | password for setting |  |  | uint32 | Read/Write | Password = 190577
270 | 2 | 28 | 4 | receiver id |  |  | uint32 | Read/Write(PW)
272 | 1 | 32 | 2 | num of node | 0-40 |  | uint16 | Read/Write
273 | 2 | 34 | 4 | node id 1 |  |  | uint32 | Read/Write
275 | 2 | 38 | 4 | node id 2 |  |  | uint32 | Read/Write
277 | 2 | 42 | 4 | node id 3 |  |  | uint32 | Read/Write
279 | 2 | 46 | 4 | node id 4 |  |  | uint32 | Read/Write
281 | 2 | 50 | 4 | node id 5 |  |  | uint32 | Read/Write
283 | 2 | 54 | 4 | node id 6 |  |  | uint32 | Read/Write
285 | 2 | 58 | 4 | node id 7 |  |  | uint32 | Read/Write
287 | 2 | 62 | 4 | node id 8 |  |  | uint32 | Read/Write
289 | 2 | 66 | 4 | node id 9 |  |  | uint32 | Read/Write
291 | 2 | 70 | 4 | node id 10 |  |  | uint32 | Read/Write
293 | 2 | 74 | 4 | node id 11 |  |  | uint32 | Read/Write
295 | 2 | 78 | 4 | node id 12 |  |  | uint32 | Read/Write
297 | 2 | 82 | 4 | node id 13 |  |  | uint32 | Read/Write
299 | 2 | 86 | 4 | node id 14 |  |  | uint32 | Read/Write
301 | 2 | 90 | 4 | node id 15 |  |  | uint32 | Read/Write
303 | 2 | 94 | 4 | node id 16 |  |  | uint32 | Read/Write
305 | 2 | 98 | 4 | node id 17 |  |  | uint32 | Read/Write
307 | 2 | 102 | 4 | node id 18 |  |  | uint32 | Read/Write
309 | 2 | 106 | 4 | node id 19 |  |  | uint32 | Read/Write
311 | 2 | 110 | 4 | node id 20 |  |  | uint32 | Read/Write
313 | 2 | 114 | 4 | node id 21 |  |  | uint32 | Read/Write
315 | 2 | 118 | 4 | node id 22 |  |  | uint32 | Read/Write
317 | 2 | 122 | 4 | node id 23 |  |  | uint32 | Read/Write
319 | 2 | 126 | 4 | node id 24 |  |  | uint32 | Read/Write
321 | 2 | 130 | 4 | node id 25 |  |  | uint32 | Read/Write
323 | 2 | 134 | 4 | node id 26 |  |  | uint32 | Read/Write
325 | 2 | 138 | 4 | node id 27 |  |  | uint32 | Read/Write
327 | 2 | 142 | 4 | node id 28 |  |  | uint32 | Read/Write
329 | 2 | 146 | 4 | node id 29 |  |  | uint32 | Read/Write
331 | 2 | 150 | 4 | node id 30 |  |  | uint32 | Read/Write
333 | 2 | 154 | 4 | node id 31 |  |  | uint32 | Read/Write
335 | 2 | 158 | 4 | node id 32 |  |  | uint32 | Read/Write
337 | 2 | 162 | 4 | node id 33 |  |  | uint32 | Read/Write
339 | 2 | 166 | 4 | node id 34 |  |  | uint32 | Read/Write
341 | 2 | 170 | 4 | node id 35 |  |  | uint32 | Read/Write
343 | 2 | 174 | 4 | node id 36 |  |  | uint32 | Read/Write
345 | 2 | 178 | 4 | node id 37 |  |  | uint32 | Read/Write
347 | 2 | 182 | 4 | node id 38 |  |  | uint32 | Read/Write
349 | 2 | 186 | 4 | node id 39 |  |  | uint32 | Read/Write
351 | 2 | 190 | 4 | node id 40 |  |  | uint32 | Read/Write
353 | 1 | 194 | 2 | cmp time 1 |  | 15 | uint16 | Read/Write | second
354 | 1 | 196 | 2 | cmp time 2 |  | 30 | uint16 | Read/Write | second
355 | 1 | 198 | 2 | cmp time 3 |  | 45 | uint16 | Read/Write | second
356 | 1 | 200 | 2 | cmp time 4 |  | 60 | uint16 | Read/Write | second
357 | 1 | 202 | 2 | cmp time 5 |  | 300 | uint16 | Read/Write | second
358 | 1 | 204 | 2 | cmp time 6 |  | 600 | uint16 | Read/Write | second
359 | 1 | 206 | 2 | cmp time 7 |  | 900 | uint16 | Read/Write | second
360 | 1 | 208 | 2 | cmp time 8 |  | 1800 | uint16 | Read/Write | second
361 | 1 | 210 | 2 | cmp time 9 |  | 3600 | uint16 | Read/Write | second
362 | 37 | 212 | 74 | spare
399 | 1 | 286 | 2 | sync all node | 0-1 |  | uint16 | Read/Write | 1: restart sync
400 | 1 | 288 | 2 | Update_enable_Node1 |  |  | hex | Read/Write | + update enable = 0xB601 = 46593 => update Cycle_wakeup, cycle_healthstatus of node + update enable = 0xB680 = 46720 => update Data_numblock, data_reg, data_numreg of node + update enable = 0xB640 = 46656 => update Offset temp, Differential Pressure, pulse width 4 channel of node + update enable = 0xB620 = 46624 => update Delta temp, Differential Pressure, counter of node
401 | 1 | 290 | 2 | Cycle_wakeup_Node1 |  |  | uint16 | Read/Write
402 | 1 | 292 | 2 | Cycle_heathsta_Node1 |  |  | uint16 | Read/Write
403 | 1 | 294 | 2 | Data_numblock_Node1 |  |  | uint16 | Read/Write
404 | 1 | 296 | 2 | Data_reg 1_Node1 |  |  | uint16 | Read/Write
405 | 1 | 298 | 2 | Data_numreg 1_Node1 |  |  | uint16 | Read/Write
406 | 1 | 300 | 2 | Data_reg 2_Node1 |  |  | uint16 | Read/Write
407 | 1 | 302 | 2 | Data_numReg 2_Node1 |  |  | uint16 | Read/Write
408 | 1 | 304 | 2 | Data_reg 3_Node1 |  |  | uint16 | Read/Write
409 | 1 | 306 | 2 | Data_numReg 3_Node1 |  |  | uint16 | Read/Write
410 | 2 | 308 | 4 | Delta_Differential Pressure_Node1 |  |  | float | Read/Write
412 | 2 | 312 | 4 | Offset_Differential Pressure_Node1 |  |  | float | Read/Write
414 | 2 | 316 | 4 | Offset_Temp_Node1 |  |  | float | Read/Write
416 | 14 | 320 | 28 | Reserve_regs_Node1 |  |  |  | Read/Write | reserve registers for node 1= 20 regs = 40 bytes
430 | 1 | 348 | 2 | Update_enable_Node2 |  |  | hex | Read/Write
431 | 1 | 350 | 2 | Cycle_wakeup_Node2 |  |  | uint16 | Read/Write
432 | 1 | 352 | 2 | Cycle_heathsta_Node2 |  |  | uint16 | Read/Write
433 | 1 | 354 | 2 | Data_numblock_Node2 |  |  | uint16 | Read/Write
434 | 1 | 356 | 2 | Data_reg 1_Node2 |  |  | uint16 | Read/Write
435 | 1 | 358 | 2 | Data_numreg 1_Node2 |  |  | uint16 | Read/Write
436 | 1 | 360 | 2 | Data_reg 2_Node2 |  |  | uint16 | Read/Write
437 | 1 | 362 | 2 | Data_numReg 2_Node2 |  |  | uint16 | Read/Write
438 | 1 | 364 | 2 | Data_reg 3_Node2 |  |  | uint16 | Read/Write
439 | 1 | 366 | 2 | Data_numReg 3_Node2 |  |  | uint16 | Read/Write
440 | 2 | 368 | 4 | Delta_Differential Pressure_Node2 |  |  | float | Read/Write
442 | 2 | 372 | 4 | Offset_Differential Pressure_Node2 |  |  | float | Read/Write
444 | 2 | 376 | 4 | Offset_Temp_Node2 |  |  | float | Read/Write
446 | 14 | 380 | 28 | Reserve_regs_Node2 |  |  |  | Read/Write
460 | 1 | 408 | 2 | Update_enable_Node3 |  |  | hex | Read/Write
461 | 1 | 410 | 2 | Cycle_wakeup_Node3 |  |  | uint16 | Read/Write
462 | 1 | 412 | 2 | Cycle_heathsta_Node3 |  |  | uint16 | Read/Write
463 | 1 | 414 | 2 | Data_numblock_Node3 |  |  | uint16 | Read/Write
464 | 1 | 416 | 2 | Data_reg 1_Node3 |  |  | uint16 | Read/Write
465 | 1 | 418 | 2 | Data_numreg 1_Node3 |  |  | uint16 | Read/Write
466 | 1 | 420 | 2 | Data_reg 2_Node3 |  |  | uint16 | Read/Write
467 | 1 | 422 | 2 | Data_numReg 2_Node3 |  |  | uint16 | Read/Write
468 | 1 | 424 | 2 | Data_reg 3_Node3 |  |  | uint16 | Read/Write
469 | 1 | 426 | 2 | Data_numReg 3_Node3 |  |  | uint16 | Read/Write
470 | 2 | 428 | 4 | Delta_Differential Pressure_Node3 |  |  | float | Read/Write
472 | 2 | 432 | 4 | Offset_Differential Pressure_Node3 |  |  | float | Read/Write
474 | 2 | 436 | 4 | Offset_Temp_Node3 |  |  | float | Read/Write
476 | 14 | 440 | 28 | Reserve_regs_Node3 |  |  |  | Read/Write
490 | 1 | 468 | 2 | Update_enable_Node4 |  |  | hex | Read/Write
491 | 1 | 470 | 2 | Cycle_wakeup_Node4 |  |  | uint16 | Read/Write
492 | 1 | 472 | 2 | Cycle_heathsta_Node4 |  |  | uint16 | Read/Write
493 | 1 | 474 | 2 | Data_numblock_Node4 |  |  | uint16 | Read/Write
494 | 1 | 476 | 2 | Data_reg 1_Node4 |  |  | uint16 | Read/Write
495 | 1 | 478 | 2 | Data_numreg 1_Node4 |  |  | uint16 | Read/Write
496 | 1 | 480 | 2 | Data_reg 2_Node4 |  |  | uint16 | Read/Write
497 | 1 | 482 | 2 | Data_numReg 2_Node4 |  |  | uint16 | Read/Write
498 | 1 | 484 | 2 | Data_reg 3_Node4 |  |  | uint16 | Read/Write
499 | 1 | 486 | 2 | Data_numReg 3_Node4 |  |  | uint16 | Read/Write
500 | 2 | 488 | 4 | Delta_Differential Pressure_Node4 |  |  | float | Read/Write
502 | 2 | 492 | 4 | Offset_Differential Pressure_Node4 |  |  | float | Read/Write
504 | 2 | 496 | 4 | Offset_Temp_Node4 |  |  | float | Read/Write
506 | 14 | 500 | 28 | Reserve_regs_Node4 |  |  |  | Read/Write
520 | 1 | 528 | 2 | Update_enable_Node5 |  |  | hex | Read/Write
521 | 1 | 530 | 2 | Cycle_wakeup_Node5 |  |  | uint16 | Read/Write
522 | 1 | 532 | 2 | Cycle_heathsta_Node5 |  |  | uint16 | Read/Write
523 | 1 | 534 | 2 | Data_numblock_Node5 |  |  | uint16 | Read/Write
524 | 1 | 536 | 2 | Data_reg 1_Node5 |  |  | uint16 | Read/Write
525 | 1 | 538 | 2 | Data_numreg 1_Node5 |  |  | uint16 | Read/Write
526 | 1 | 540 | 2 | Data_reg 2_Node5 |  |  | uint16 | Read/Write
527 | 1 | 542 | 2 | Data_numReg 2_Node5 |  |  | uint16 | Read/Write
528 | 1 | 544 | 2 | Data_reg 3_Node5 |  |  | uint16 | Read/Write
529 | 1 | 546 | 2 | Data_numReg 3_Node5 |  |  | uint16 | Read/Write
530 | 2 | 548 | 4 | Delta_Differential Pressure_Node5 |  |  | float | Read/Write
532 | 2 | 552 | 4 | Offset_Differential Pressure_Node5 |  |  | float | Read/Write
534 | 2 | 556 | 4 | Offset_Temp_Node5 |  |  | float | Read/Write
536 | 14 | 560 | 28 | Reserve_regs_Node5 |  |  |  | Read/Write
550 | 1 | 588 | 2 | Update_enable_Node6 |  |  | hex | Read/Write
551 | 1 | 590 | 2 | Cycle_wakeup_Node6 |  |  | uint16 | Read/Write
552 | 1 | 592 | 2 | Cycle_heathsta_Node6 |  |  | uint16 | Read/Write
553 | 1 | 594 | 2 | Data_numblock_Node6 |  |  | uint16 | Read/Write
554 | 1 | 596 | 2 | Data_reg 1_Node6 |  |  | uint16 | Read/Write
555 | 1 | 598 | 2 | Data_numreg 1_Node6 |  |  | uint16 | Read/Write
556 | 1 | 600 | 2 | Data_reg 2_Node6 |  |  | uint16 | Read/Write
557 | 1 | 602 | 2 | Data_numReg 2_Node6 |  |  | uint16 | Read/Write
558 | 1 | 604 | 2 | Data_reg 3_Node6 |  |  | uint16 | Read/Write
559 | 1 | 606 | 2 | Data_numReg 3_Node6 |  |  | uint16 | Read/Write
560 | 2 | 608 | 4 | Delta_Differential Pressure_Node6 |  |  | float | Read/Write
562 | 2 | 612 | 4 | Offset_Differential Pressure_Node6 |  |  | float | Read/Write
564 | 2 | 616 | 4 | Offset_Temp_Node6 |  |  | float | Read/Write
566 | 14 | 620 | 28 | Reserve_regs_Node6 |  |  |  | Read/Write
580 | 1 | 648 | 2 | Update_enable_Node7 |  |  | hex | Read/Write
581 | 1 | 650 | 2 | Cycle_wakeup_Node7 |  |  | uint16 | Read/Write
582 | 1 | 652 | 2 | Cycle_heathsta_Node7 |  |  | uint16 | Read/Write
583 | 1 | 654 | 2 | Data_numblock_Node7 |  |  | uint16 | Read/Write
584 | 1 | 656 | 2 | Data_reg 1_Node7 |  |  | uint16 | Read/Write
585 | 1 | 658 | 2 | Data_numreg 1_Node7 |  |  | uint16 | Read/Write
586 | 1 | 660 | 2 | Data_reg 2_Node7 |  |  | uint16 | Read/Write
587 | 1 | 662 | 2 | Data_numReg 2_Node7 |  |  | uint16 | Read/Write
588 | 1 | 664 | 2 | Data_reg 3_Node7 |  |  | uint16 | Read/Write
589 | 1 | 666 | 2 | Data_numReg 3_Node7 |  |  | uint16 | Read/Write
590 | 2 | 668 | 4 | Delta_Differential Pressure_Node7 |  |  | float | Read/Write
592 | 2 | 672 | 4 | Offset_Differential Pressure_Node7 |  |  | float | Read/Write
594 | 2 | 676 | 4 | Offset_Temp_Node7 |  |  | float | Read/Write
596 | 14 | 680 | 28 | Reserve_regs_Node7 |  |  |  | Read/Write
610 | 1 | 708 | 2 | Update_enable_Node8 |  |  | hex | Read/Write
611 | 1 | 710 | 2 | Cycle_wakeup_Node8 |  |  | uint16 | Read/Write
612 | 1 | 712 | 2 | Cycle_heathsta_Node8 |  |  | uint16 | Read/Write
613 | 1 | 714 | 2 | Data_numblock_Node8 |  |  | uint16 | Read/Write
614 | 1 | 716 | 2 | Data_reg 1_Node8 |  |  | uint16 | Read/Write
615 | 1 | 718 | 2 | Data_numreg 1_Node8 |  |  | uint16 | Read/Write
616 | 1 | 720 | 2 | Data_reg 2_Node8 |  |  | uint16 | Read/Write
617 | 1 | 722 | 2 | Data_numReg 2_Node8 |  |  | uint16 | Read/Write
618 | 1 | 724 | 2 | Data_reg 3_Node8 |  |  | uint16 | Read/Write
619 | 1 | 726 | 2 | Data_numReg 3_Node8 |  |  | uint16 | Read/Write
620 | 2 | 728 | 4 | Delta_Differential Pressure_Node8 |  |  | float | Read/Write
622 | 2 | 732 | 4 | Offset_Differential Pressure_Node8 |  |  | float | Read/Write
624 | 2 | 736 | 4 | Offset_Temp_Node8 |  |  | float | Read/Write
626 | 14 | 740 | 28 | Reserve_regs_Node8 |  |  |  | Read/Write
640 | 1 | 768 | 2 | Update_enable_Node9 |  |  | hex | Read/Write
641 | 1 | 770 | 2 | Cycle_wakeup_Node9 |  |  | uint16 | Read/Write
642 | 1 | 772 | 2 | Cycle_heathsta_Node9 |  |  | uint16 | Read/Write
643 | 1 | 774 | 2 | Data_numblock_Node9 |  |  | uint16 | Read/Write
644 | 1 | 776 | 2 | Data_reg 1_Node9 |  |  | uint16 | Read/Write
645 | 1 | 778 | 2 | Data_numreg 1_Node9 |  |  | uint16 | Read/Write
646 | 1 | 780 | 2 | Data_reg 2_Node9 |  |  | uint16 | Read/Write
647 | 1 | 782 | 2 | Data_numReg 2_Node9 |  |  | uint16 | Read/Write
648 | 1 | 784 | 2 | Data_reg 3_Node9 |  |  | uint16 | Read/Write
649 | 1 | 786 | 2 | Data_numReg 3_Node9 |  |  | uint16 | Read/Write
650 | 2 | 788 | 4 | Delta_Differential Pressure_Node9 |  |  | float | Read/Write
652 | 2 | 792 | 4 | Offset_Differential Pressure_Node9 |  |  | float | Read/Write
654 | 2 | 796 | 4 | Offset_Temp_Node9 |  |  | float | Read/Write
656 | 14 | 800 | 28 | Reserve_regs_Node9 |  |  |  | Read/Write
670 | 1 | 828 | 2 | Update_enable_Node10 |  |  | hex | Read/Write
671 | 1 | 830 | 2 | Cycle_wakeup_Node10 |  |  | uint16 | Read/Write
672 | 1 | 832 | 2 | Cycle_heathsta_Node10 |  |  | uint16 | Read/Write
673 | 1 | 834 | 2 | Data_numblock_Node10 |  |  | uint16 | Read/Write
674 | 1 | 836 | 2 | Data_reg 1_Node10 |  |  | uint16 | Read/Write
675 | 1 | 838 | 2 | Data_numreg 1_Node10 |  |  | uint16 | Read/Write
676 | 1 | 840 | 2 | Data_reg 2_Node10 |  |  | uint16 | Read/Write
677 | 1 | 842 | 2 | Data_numReg 2_Node10 |  |  | uint16 | Read/Write
678 | 1 | 844 | 2 | Data_reg 3_Node10 |  |  | uint16 | Read/Write
679 | 1 | 846 | 2 | Data_numReg 3_Node10 |  |  | uint16 | Read/Write
680 | 2 | 848 | 4 | Delta_Differential Pressure_Node10 |  |  | float | Read/Write
682 | 2 | 852 | 4 | Offset_Differential Pressure_Node10 |  |  | float | Read/Write
684 | 2 | 856 | 4 | Offset_Temp_Node10 |  |  | float | Read/Write
686 | 14 | 860 | 28 | Reserve_regs_Node10 |  |  |  | Read/Write
700 | 1 | 888 | 2 | Update_enable_Node11 |  |  | hex | Read/Write
701 | 1 | 890 | 2 | Cycle_wakeup_Node11 |  |  | uint16 | Read/Write
702 | 1 | 892 | 2 | Cycle_heathsta_Node11 |  |  | uint16 | Read/Write
703 | 1 | 894 | 2 | Data_numblock_Node11 |  |  | uint16 | Read/Write
704 | 1 | 896 | 2 | Data_reg 1_Node11 |  |  | uint16 | Read/Write
705 | 1 | 898 | 2 | Data_numreg 1_Node11 |  |  | uint16 | Read/Write
706 | 1 | 900 | 2 | Data_reg 2_Node11 |  |  | uint16 | Read/Write
707 | 1 | 902 | 2 | Data_numReg 2_Node11 |  |  | uint16 | Read/Write
708 | 1 | 904 | 2 | Data_reg 3_Node11 |  |  | uint16 | Read/Write
709 | 1 | 906 | 2 | Data_numReg 3_Node11 |  |  | uint16 | Read/Write
710 | 2 | 908 | 4 | Delta_Differential Pressure_Node11 |  |  | float | Read/Write
712 | 2 | 912 | 4 | Offset_Differential Pressure_Node11 |  |  | float | Read/Write
714 | 2 | 916 | 4 | Offset_Temp_Node11 |  |  | float | Read/Write
716 | 14 | 920 | 28 | Reserve_regs_Node11 |  |  |  | Read/Write
730 | 1 | 948 | 2 | Update_enable_Node12 |  |  | hex | Read/Write
731 | 1 | 950 | 2 | Cycle_wakeup_Node12 |  |  | uint16 | Read/Write
732 | 1 | 952 | 2 | Cycle_heathsta_Node12 |  |  | uint16 | Read/Write
733 | 1 | 954 | 2 | Data_numblock_Node12 |  |  | uint16 | Read/Write
734 | 1 | 956 | 2 | Data_reg 1_Node12 |  |  | uint16 | Read/Write
735 | 1 | 958 | 2 | Data_numreg 1_Node12 |  |  | uint16 | Read/Write
736 | 1 | 960 | 2 | Data_reg 2_Node12 |  |  | uint16 | Read/Write
737 | 1 | 962 | 2 | Data_numReg 2_Node12 |  |  | uint16 | Read/Write
738 | 1 | 964 | 2 | Data_reg 3_Node12 |  |  | uint16 | Read/Write
739 | 1 | 966 | 2 | Data_numReg 3_Node12 |  |  | uint16 | Read/Write
740 | 2 | 968 | 4 | Delta_Differential Pressure_Node12 |  |  | float | Read/Write
742 | 2 | 972 | 4 | Offset_Differential Pressure_Node12 |  |  | float | Read/Write
744 | 2 | 976 | 4 | Offset_Temp_Node12 |  |  | float | Read/Write
746 | 14 | 980 | 28 | Reserve_regs_Node12 |  |  |  | Read/Write
760 | 1 | 1008 | 2 | Update_enable_Node13 |  |  | hex | Read/Write
761 | 1 | 1010 | 2 | Cycle_wakeup_Node13 |  |  | uint16 | Read/Write
762 | 1 | 1012 | 2 | Cycle_heathsta_Node13 |  |  | uint16 | Read/Write
763 | 1 | 1014 | 2 | Data_numblock_Node13 |  |  | uint16 | Read/Write
764 | 1 | 1016 | 2 | Data_reg 1_Node13 |  |  | uint16 | Read/Write
765 | 1 | 1018 | 2 | Data_numreg 1_Node13 |  |  | uint16 | Read/Write
766 | 1 | 1020 | 2 | Data_reg 2_Node13 |  |  | uint16 | Read/Write
767 | 1 | 1022 | 2 | Data_numReg 2_Node13 |  |  | uint16 | Read/Write
768 | 1 | 1024 | 2 | Data_reg 3_Node13 |  |  | uint16 | Read/Write
769 | 1 | 1026 | 2 | Data_numReg 3_Node13 |  |  | uint16 | Read/Write
770 | 2 | 1028 | 4 | Delta_Differential Pressure_Node13 |  |  | float | Read/Write
772 | 2 | 1032 | 4 | Offset_Differential Pressure_Node13 |  |  | float | Read/Write
774 | 2 | 1036 | 4 | Offset_Temp_Node13 |  |  | float | Read/Write
776 | 14 | 1040 | 28 | Reserve_regs_Node13 |  |  |  | Read/Write
790 | 1 | 1068 | 2 | Update_enable_Node14 |  |  | hex | Read/Write
791 | 1 | 1070 | 2 | Cycle_wakeup_Node14 |  |  | uint16 | Read/Write
792 | 1 | 1072 | 2 | Cycle_heathsta_Node14 |  |  | uint16 | Read/Write
793 | 1 | 1074 | 2 | Data_numblock_Node14 |  |  | uint16 | Read/Write
794 | 1 | 1076 | 2 | Data_reg 1_Node14 |  |  | uint16 | Read/Write
795 | 1 | 1078 | 2 | Data_numreg 1_Node14 |  |  | uint16 | Read/Write
796 | 1 | 1080 | 2 | Data_reg 2_Node14 |  |  | uint16 | Read/Write
797 | 1 | 1082 | 2 | Data_numReg 2_Node14 |  |  | uint16 | Read/Write
798 | 1 | 1084 | 2 | Data_reg 3_Node14 |  |  | uint16 | Read/Write
799 | 1 | 1086 | 2 | Data_numReg 3_Node14 |  |  | uint16 | Read/Write
800 | 2 | 1088 | 4 | Delta_Differential Pressure_Node14 |  |  | float | Read/Write
802 | 2 | 1092 | 4 | Offset_Differential Pressure_Node14 |  |  | float | Read/Write
804 | 2 | 1096 | 4 | Offset_Temp_Node14 |  |  | float | Read/Write
806 | 14 | 1100 | 28 | Reserve_regs_Node14 |  |  |  | Read/Write
820 | 1 | 1128 | 2 | Update_enable_Node15 |  |  | hex | Read/Write
821 | 1 | 1130 | 2 | Cycle_wakeup_Node15 |  |  | uint16 | Read/Write
822 | 1 | 1132 | 2 | Cycle_heathsta_Node15 |  |  | uint16 | Read/Write
823 | 1 | 1134 | 2 | Data_numblock_Node15 |  |  | uint16 | Read/Write
824 | 1 | 1136 | 2 | Data_reg 1_Node15 |  |  | uint16 | Read/Write
825 | 1 | 1138 | 2 | Data_numreg 1_Node15 |  |  | uint16 | Read/Write
826 | 1 | 1140 | 2 | Data_reg 2_Node15 |  |  | uint16 | Read/Write
827 | 1 | 1142 | 2 | Data_numReg 2_Node15 |  |  | uint16 | Read/Write
828 | 1 | 1144 | 2 | Data_reg 3_Node15 |  |  | uint16 | Read/Write
829 | 1 | 1146 | 2 | Data_numReg 3_Node15 |  |  | uint16 | Read/Write
830 | 2 | 1148 | 4 | Delta_Differential Pressure_Node15 |  |  | float | Read/Write
832 | 2 | 1152 | 4 | Offset_Differential Pressure_Node15 |  |  | float | Read/Write
834 | 2 | 1156 | 4 | Offset_Temp_Node15 |  |  | float | Read/Write
836 | 14 | 1160 | 28 | Reserve_regs_Node15 |  |  |  | Read/Write
850 | 1 | 1188 | 2 | Update_enable_Node16 |  |  | hex | Read/Write
851 | 1 | 1190 | 2 | Cycle_wakeup_Node16 |  |  | uint16 | Read/Write
852 | 1 | 1192 | 2 | Cycle_heathsta_Node16 |  |  | uint16 | Read/Write
853 | 1 | 1194 | 2 | Data_numblock_Node16 |  |  | uint16 | Read/Write
854 | 1 | 1196 | 2 | Data_reg 1_Node16 |  |  | uint16 | Read/Write
855 | 1 | 1198 | 2 | Data_numreg 1_Node16 |  |  | uint16 | Read/Write
856 | 1 | 1200 | 2 | Data_reg 2_Node16 |  |  | uint16 | Read/Write
857 | 1 | 1202 | 2 | Data_numReg 2_Node16 |  |  | uint16 | Read/Write
858 | 1 | 1204 | 2 | Data_reg 3_Node16 |  |  | uint16 | Read/Write
859 | 1 | 1206 | 2 | Data_numReg 3_Node16 |  |  | uint16 | Read/Write
860 | 2 | 1208 | 4 | Delta_Differential Pressure_Node16 |  |  | float | Read/Write
862 | 2 | 1212 | 4 | Offset_Differential Pressure_Node16 |  |  | float | Read/Write
864 | 2 | 1216 | 4 | Offset_Temp_Node16 |  |  | float | Read/Write
866 | 14 | 1220 | 28 | Reserve_regs_Node16 |  |  |  | Read/Write
880 | 1 | 1248 | 2 | Update_enable_Node17 |  |  | hex | Read/Write
881 | 1 | 1250 | 2 | Cycle_wakeup_Node17 |  |  | uint16 | Read/Write
882 | 1 | 1252 | 2 | Cycle_heathsta_Node17 |  |  | uint16 | Read/Write
883 | 1 | 1254 | 2 | Data_numblock_Node17 |  |  | uint16 | Read/Write
884 | 1 | 1256 | 2 | Data_reg 1_Node17 |  |  | uint16 | Read/Write
885 | 1 | 1258 | 2 | Data_numreg 1_Node17 |  |  | uint16 | Read/Write
886 | 1 | 1260 | 2 | Data_reg 2_Node17 |  |  | uint16 | Read/Write
887 | 1 | 1262 | 2 | Data_numReg 2_Node17 |  |  | uint16 | Read/Write
888 | 1 | 1264 | 2 | Data_reg 3_Node17 |  |  | uint16 | Read/Write
889 | 1 | 1266 | 2 | Data_numReg 3_Node17 |  |  | uint16 | Read/Write
890 | 2 | 1268 | 4 | Delta_Differential Pressure_Node17 |  |  | float | Read/Write
892 | 2 | 1272 | 4 | Offset_Differential Pressure_Node17 |  |  | float | Read/Write
894 | 2 | 1276 | 4 | Offset_Temp_Node17 |  |  | float | Read/Write
896 | 14 | 1280 | 28 | Reserve_regs_Node17 |  |  |  | Read/Write
910 | 1 | 1308 | 2 | Update_enable_Node18 |  |  | hex | Read/Write
911 | 1 | 1310 | 2 | Cycle_wakeup_Node18 |  |  | uint16 | Read/Write
912 | 1 | 1312 | 2 | Cycle_heathsta_Node18 |  |  | uint16 | Read/Write
913 | 1 | 1314 | 2 | Data_numblock_Node18 |  |  | uint16 | Read/Write
914 | 1 | 1316 | 2 | Data_reg 1_Node18 |  |  | uint16 | Read/Write
915 | 1 | 1318 | 2 | Data_numreg 1_Node18 |  |  | uint16 | Read/Write
916 | 1 | 1320 | 2 | Data_reg 2_Node18 |  |  | uint16 | Read/Write
917 | 1 | 1322 | 2 | Data_numReg 2_Node18 |  |  | uint16 | Read/Write
918 | 1 | 1324 | 2 | Data_reg 3_Node18 |  |  | uint16 | Read/Write
919 | 1 | 1326 | 2 | Data_numReg 3_Node18 |  |  | uint16 | Read/Write
920 | 2 | 1328 | 4 | Delta_Differential Pressure_Node18 |  |  | float | Read/Write
922 | 2 | 1332 | 4 | Offset_Differential Pressure_Node18 |  |  | float | Read/Write
924 | 2 | 1336 | 4 | Offset_Temp_Node18 |  |  | float | Read/Write
926 | 14 | 1340 | 28 | Reserve_regs_Node18 |  |  |  | Read/Write
940 | 1 | 1368 | 2 | Update_enable_Node19 |  |  | hex | Read/Write
941 | 1 | 1370 | 2 | Cycle_wakeup_Node19 |  |  | uint16 | Read/Write
942 | 1 | 1372 | 2 | Cycle_heathsta_Node19 |  |  | uint16 | Read/Write
943 | 1 | 1374 | 2 | Data_numblock_Node19 |  |  | uint16 | Read/Write
944 | 1 | 1376 | 2 | Data_reg 1_Node19 |  |  | uint16 | Read/Write
945 | 1 | 1378 | 2 | Data_numreg 1_Node19 |  |  | uint16 | Read/Write
946 | 1 | 1380 | 2 | Data_reg 2_Node19 |  |  | uint16 | Read/Write
947 | 1 | 1382 | 2 | Data_numReg 2_Node19 |  |  | uint16 | Read/Write
948 | 1 | 1384 | 2 | Data_reg 3_Node19 |  |  | uint16 | Read/Write
949 | 1 | 1386 | 2 | Data_numReg 3_Node19 |  |  | uint16 | Read/Write
950 | 2 | 1388 | 4 | Delta_Differential Pressure_Node19 |  |  | float | Read/Write
952 | 2 | 1392 | 4 | Offset_Differential Pressure_Node19 |  |  | float | Read/Write
954 | 2 | 1396 | 4 | Offset_Temp_Node19 |  |  | float | Read/Write
956 | 14 | 1400 | 28 | Reserve_regs_Node19 |  |  |  | Read/Write
970 | 1 | 1428 | 2 | Update_enable_Node20 |  |  | hex | Read/Write
971 | 1 | 1430 | 2 | Cycle_wakeup_Node20 |  |  | uint16 | Read/Write
972 | 1 | 1432 | 2 | Cycle_heathsta_Node20 |  |  | uint16 | Read/Write
973 | 1 | 1434 | 2 | Data_numblock_Node20 |  |  | uint16 | Read/Write
974 | 1 | 1436 | 2 | Data_reg 1_Node20 |  |  | uint16 | Read/Write
975 | 1 | 1438 | 2 | Data_numreg 1_Node20 |  |  | uint16 | Read/Write
976 | 1 | 1440 | 2 | Data_reg 2_Node20 |  |  | uint16 | Read/Write
977 | 1 | 1442 | 2 | Data_numReg 2_Node20 |  |  | uint16 | Read/Write
978 | 1 | 1444 | 2 | Data_reg 3_Node20 |  |  | uint16 | Read/Write
979 | 1 | 1446 | 2 | Data_numReg 3_Node20 |  |  | uint16 | Read/Write
980 | 2 | 1448 | 4 | Delta_Differential Pressure_Node20 |  |  | float | Read/Write
982 | 2 | 1452 | 4 | Offset_Differential Pressure_Node20 |  |  | float | Read/Write
984 | 2 | 1456 | 4 | Offset_Temp_Node20 |  |  | float | Read/Write
986 | 14 | 1460 | 28 | Reserve_regs_Node20 |  |  |  | Read/Write
1000 | 1 | 1488 | 2 | Update_enable_Node21 |  |  | hex | Read/Write
1001 | 1 | 1490 | 2 | Cycle_wakeup_Node21 |  |  | uint16 | Read/Write
1002 | 1 | 1492 | 2 | Cycle_heathsta_Node21 |  |  | uint16 | Read/Write
1003 | 1 | 1494 | 2 | Data_numblock_Node21 |  |  | uint16 | Read/Write
1004 | 1 | 1496 | 2 | Data_reg 1_Node21 |  |  | uint16 | Read/Write
1005 | 1 | 1498 | 2 | Data_numreg 1_Node21 |  |  | uint16 | Read/Write
1006 | 1 | 1500 | 2 | Data_reg 2_Node21 |  |  | uint16 | Read/Write
1007 | 1 | 1502 | 2 | Data_numReg 2_Node21 |  |  | uint16 | Read/Write
1008 | 1 | 1504 | 2 | Data_reg 3_Node21 |  |  | uint16 | Read/Write
1009 | 1 | 1506 | 2 | Data_numReg 3_Node21 |  |  | uint16 | Read/Write
1010 | 2 | 1508 | 4 | Delta_Differential Pressure_Node21 |  |  | float | Read/Write
1012 | 2 | 1512 | 4 | Offset_Differential Pressure_Node21 |  |  | float | Read/Write
1014 | 2 | 1516 | 4 | Offset_Temp_Node21 |  |  | float | Read/Write
1016 | 14 | 1520 | 28 | Reserve_regs_Node21 |  |  |  | Read/Write
1030 | 1 | 1548 | 2 | Update_enable_Node22 |  |  | hex | Read/Write
1031 | 1 | 1550 | 2 | Cycle_wakeup_Node22 |  |  | uint16 | Read/Write
1032 | 1 | 1552 | 2 | Cycle_heathsta_Node22 |  |  | uint16 | Read/Write
1033 | 1 | 1554 | 2 | Data_numblock_Node22 |  |  | uint16 | Read/Write
1034 | 1 | 1556 | 2 | Data_reg 1_Node22 |  |  | uint16 | Read/Write
1035 | 1 | 1558 | 2 | Data_numreg 1_Node22 |  |  | uint16 | Read/Write
1036 | 1 | 1560 | 2 | Data_reg 2_Node22 |  |  | uint16 | Read/Write
1037 | 1 | 1562 | 2 | Data_numReg 2_Node22 |  |  | uint16 | Read/Write
1038 | 1 | 1564 | 2 | Data_reg 3_Node22 |  |  | uint16 | Read/Write
1039 | 1 | 1566 | 2 | Data_numReg 3_Node22 |  |  | uint16 | Read/Write
1040 | 2 | 1568 | 4 | Delta_Differential Pressure_Node22 |  |  | float | Read/Write
1042 | 2 | 1572 | 4 | Offset_Differential Pressure_Node22 |  |  | float | Read/Write
1044 | 2 | 1576 | 4 | Offset_Temp_Node22 |  |  | float | Read/Write
1046 | 14 | 1580 | 28 | Reserve_regs_Node22 |  |  |  | Read/Write
1060 | 1 | 1608 | 2 | Update_enable_Node23 |  |  | hex | Read/Write
1061 | 1 | 1610 | 2 | Cycle_wakeup_Node23 |  |  | uint16 | Read/Write
1062 | 1 | 1612 | 2 | Cycle_heathsta_Node23 |  |  | uint16 | Read/Write
1063 | 1 | 1614 | 2 | Data_numblock_Node23 |  |  | uint16 | Read/Write
1064 | 1 | 1616 | 2 | Data_reg 1_Node23 |  |  | uint16 | Read/Write
1065 | 1 | 1618 | 2 | Data_numreg 1_Node23 |  |  | uint16 | Read/Write
1066 | 1 | 1620 | 2 | Data_reg 2_Node23 |  |  | uint16 | Read/Write
1067 | 1 | 1622 | 2 | Data_numReg 2_Node23 |  |  | uint16 | Read/Write
1068 | 1 | 1624 | 2 | Data_reg 3_Node23 |  |  | uint16 | Read/Write
1069 | 1 | 1626 | 2 | Data_numReg 3_Node23 |  |  | uint16 | Read/Write
1070 | 2 | 1628 | 4 | Delta_Differential Pressure_Node23 |  |  | float | Read/Write
1072 | 2 | 1632 | 4 | Offset_Differential Pressure_Node23 |  |  | float | Read/Write
1074 | 2 | 1636 | 4 | Offset_Temp_Node23 |  |  | float | Read/Write
1076 | 14 | 1640 | 28 | Reserve_regs_Node23 |  |  |  | Read/Write
1090 | 1 | 1668 | 2 | Update_enable_Node24 |  |  | hex | Read/Write
1091 | 1 | 1670 | 2 | Cycle_wakeup_Node24 |  |  | uint16 | Read/Write
1092 | 1 | 1672 | 2 | Cycle_heathsta_Node24 |  |  | uint16 | Read/Write
1093 | 1 | 1674 | 2 | Data_numblock_Node24 |  |  | uint16 | Read/Write
1094 | 1 | 1676 | 2 | Data_reg 1_Node24 |  |  | uint16 | Read/Write
1095 | 1 | 1678 | 2 | Data_numreg 1_Node24 |  |  | uint16 | Read/Write
1096 | 1 | 1680 | 2 | Data_reg 2_Node24 |  |  | uint16 | Read/Write
1097 | 1 | 1682 | 2 | Data_numReg 2_Node24 |  |  | uint16 | Read/Write
1098 | 1 | 1684 | 2 | Data_reg 3_Node24 |  |  | uint16 | Read/Write
1099 | 1 | 1686 | 2 | Data_numReg 3_Node24 |  |  | uint16 | Read/Write
1100 | 2 | 1688 | 4 | Delta_Differential Pressure_Node24 |  |  | float | Read/Write
1102 | 2 | 1692 | 4 | Offset_Differential Pressure_Node24 |  |  | float | Read/Write
1104 | 2 | 1696 | 4 | Offset_Temp_Node24 |  |  | float | Read/Write
1106 | 14 | 1700 | 28 | Reserve_regs_Node24 |  |  |  | Read/Write
1120 | 1 | 1728 | 2 | Update_enable_Node25 |  |  | hex | Read/Write
1121 | 1 | 1730 | 2 | Cycle_wakeup_Node25 |  |  | uint16 | Read/Write
1122 | 1 | 1732 | 2 | Cycle_heathsta_Node25 |  |  | uint16 | Read/Write
1123 | 1 | 1734 | 2 | Data_numblock_Node25 |  |  | uint16 | Read/Write
1124 | 1 | 1736 | 2 | Data_reg 1_Node25 |  |  | uint16 | Read/Write
1125 | 1 | 1738 | 2 | Data_numreg 1_Node25 |  |  | uint16 | Read/Write
1126 | 1 | 1740 | 2 | Data_reg 2_Node25 |  |  | uint16 | Read/Write
1127 | 1 | 1742 | 2 | Data_numReg 2_Node25 |  |  | uint16 | Read/Write
1128 | 1 | 1744 | 2 | Data_reg 3_Node25 |  |  | uint16 | Read/Write
1129 | 1 | 1746 | 2 | Data_numReg 3_Node25 |  |  | uint16 | Read/Write
1130 | 2 | 1748 | 4 | Delta_Differential Pressure_Node25 |  |  | float | Read/Write
1132 | 2 | 1752 | 4 | Offset_Differential Pressure_Node25 |  |  | float | Read/Write
1134 | 2 | 1756 | 4 | Offset_Temp_Node25 |  |  | float | Read/Write
1136 | 14 | 1760 | 28 | Reserve_regs_Node25 |  |  |  | Read/Write
1150 | 1 | 1788 | 2 | Update_enable_Node26 |  |  | hex | Read/Write
1151 | 1 | 1790 | 2 | Cycle_wakeup_Node26 |  |  | uint16 | Read/Write
1152 | 1 | 1792 | 2 | Cycle_heathsta_Node26 |  |  | uint16 | Read/Write
1153 | 1 | 1794 | 2 | Data_numblock_Node26 |  |  | uint16 | Read/Write
1154 | 1 | 1796 | 2 | Data_reg 1_Node26 |  |  | uint16 | Read/Write
1155 | 1 | 1798 | 2 | Data_numreg 1_Node26 |  |  | uint16 | Read/Write
1156 | 1 | 1800 | 2 | Data_reg 2_Node26 |  |  | uint16 | Read/Write
1157 | 1 | 1802 | 2 | Data_numReg 2_Node26 |  |  | uint16 | Read/Write
1158 | 1 | 1804 | 2 | Data_reg 3_Node26 |  |  | uint16 | Read/Write
1159 | 1 | 1806 | 2 | Data_numReg 3_Node26 |  |  | uint16 | Read/Write
1160 | 2 | 1808 | 4 | Delta_Differential Pressure_Node26 |  |  | float | Read/Write
1162 | 2 | 1812 | 4 | Offset_Differential Pressure_Node26 |  |  | float | Read/Write
1164 | 2 | 1816 | 4 | Offset_Temp_Node26 |  |  | float | Read/Write
1166 | 14 | 1820 | 28 | Reserve_regs_Node26 |  |  |  | Read/Write
1180 | 1 | 1848 | 2 | Update_enable_Node27 |  |  | hex | Read/Write
1181 | 1 | 1850 | 2 | Cycle_wakeup_Node27 |  |  | uint16 | Read/Write
1182 | 1 | 1852 | 2 | Cycle_heathsta_Node27 |  |  | uint16 | Read/Write
1183 | 1 | 1854 | 2 | Data_numblock_Node27 |  |  | uint16 | Read/Write
1184 | 1 | 1856 | 2 | Data_reg 1_Node27 |  |  | uint16 | Read/Write
1185 | 1 | 1858 | 2 | Data_numreg 1_Node27 |  |  | uint16 | Read/Write
1186 | 1 | 1860 | 2 | Data_reg 2_Node27 |  |  | uint16 | Read/Write
1187 | 1 | 1862 | 2 | Data_numReg 2_Node27 |  |  | uint16 | Read/Write
1188 | 1 | 1864 | 2 | Data_reg 3_Node27 |  |  | uint16 | Read/Write
1189 | 1 | 1866 | 2 | Data_numReg 3_Node27 |  |  | uint16 | Read/Write
1190 | 2 | 1868 | 4 | Delta_Differential Pressure_Node27 |  |  | float | Read/Write
1192 | 2 | 1872 | 4 | Offset_Differential Pressure_Node27 |  |  | float | Read/Write
1194 | 2 | 1876 | 4 | Offset_Temp_Node27 |  |  | float | Read/Write
1196 | 14 | 1880 | 28 | Reserve_regs_Node27 |  |  |  | Read/Write
1210 | 1 | 1908 | 2 | Update_enable_Node28 |  |  | hex | Read/Write
1211 | 1 | 1910 | 2 | Cycle_wakeup_Node28 |  |  | uint16 | Read/Write
1212 | 1 | 1912 | 2 | Cycle_heathsta_Node28 |  |  | uint16 | Read/Write
1213 | 1 | 1914 | 2 | Data_numblock_Node28 |  |  | uint16 | Read/Write
1214 | 1 | 1916 | 2 | Data_reg 1_Node28 |  |  | uint16 | Read/Write
1215 | 1 | 1918 | 2 | Data_numreg 1_Node28 |  |  | uint16 | Read/Write
1216 | 1 | 1920 | 2 | Data_reg 2_Node28 |  |  | uint16 | Read/Write
1217 | 1 | 1922 | 2 | Data_numReg 2_Node28 |  |  | uint16 | Read/Write
1218 | 1 | 1924 | 2 | Data_reg 3_Node28 |  |  | uint16 | Read/Write
1219 | 1 | 1926 | 2 | Data_numReg 3_Node28 |  |  | uint16 | Read/Write
1220 | 2 | 1928 | 4 | Delta_Differential Pressure_Node28 |  |  | float | Read/Write
1222 | 2 | 1932 | 4 | Offset_Differential Pressure_Node28 |  |  | float | Read/Write
1224 | 2 | 1936 | 4 | Offset_Temp_Node28 |  |  | float | Read/Write
1226 | 14 | 1940 | 28 | Reserve_regs_Node28 |  |  |  | Read/Write
1240 | 1 | 1968 | 2 | Update_enable_Node29 |  |  | hex | Read/Write
1241 | 1 | 1970 | 2 | Cycle_wakeup_Node29 |  |  | uint16 | Read/Write
1242 | 1 | 1972 | 2 | Cycle_heathsta_Node29 |  |  | uint16 | Read/Write
1243 | 1 | 1974 | 2 | Data_numblock_Node29 |  |  | uint16 | Read/Write
1244 | 1 | 1976 | 2 | Data_reg 1_Node29 |  |  | uint16 | Read/Write
1245 | 1 | 1978 | 2 | Data_numreg 1_Node29 |  |  | uint16 | Read/Write
1246 | 1 | 1980 | 2 | Data_reg 2_Node29 |  |  | uint16 | Read/Write
1247 | 1 | 1982 | 2 | Data_numReg 2_Node29 |  |  | uint16 | Read/Write
1248 | 1 | 1984 | 2 | Data_reg 3_Node29 |  |  | uint16 | Read/Write
1249 | 1 | 1986 | 2 | Data_numReg 3_Node29 |  |  | uint16 | Read/Write
1250 | 2 | 1988 | 4 | Delta_Differential Pressure_Node29 |  |  | float | Read/Write
1252 | 2 | 1992 | 4 | Offset_Differential Pressure_Node29 |  |  | float | Read/Write
1254 | 2 | 1996 | 4 | Offset_Temp_Node29 |  |  | float | Read/Write
1256 | 14 | 2000 | 28 | Reserve_regs_Node29 |  |  |  | Read/Write
1270 | 1 | 2028 | 2 | Update_enable_Node30 |  |  | hex | Read/Write
1271 | 1 | 2030 | 2 | Cycle_wakeup_Node30 |  |  | uint16 | Read/Write
1272 | 1 | 2032 | 2 | Cycle_heathsta_Node30 |  |  | uint16 | Read/Write
1273 | 1 | 2034 | 2 | Data_numblock_Node30 |  |  | uint16 | Read/Write
1274 | 1 | 2036 | 2 | Data_reg 1_Node30 |  |  | uint16 | Read/Write
1275 | 1 | 2038 | 2 | Data_numreg 1_Node30 |  |  | uint16 | Read/Write
1276 | 1 | 2040 | 2 | Data_reg 2_Node30 |  |  | uint16 | Read/Write
1277 | 1 | 2042 | 2 | Data_numReg 2_Node30 |  |  | uint16 | Read/Write
1278 | 1 | 2044 | 2 | Data_reg 3_Node30 |  |  | uint16 | Read/Write
1279 | 1 | 2046 | 2 | Data_numReg 3_Node30 |  |  | uint16 | Read/Write
1280 | 2 | 2048 | 4 | Delta_Differential Pressure_Node30 |  |  | float | Read/Write
1282 | 2 | 2052 | 4 | Offset_Differential Pressure_Node30 |  |  | float | Read/Write
1284 | 2 | 2056 | 4 | Offset_Temp_Node30 |  |  | float | Read/Write
1286 | 14 | 2060 | 28 | Reserve_regs_Node30 |  |  |  | Read/Write
1300 | 1 | 2088 | 2 | Update_enable_Node31 |  |  | hex | Read/Write
1301 | 1 | 2090 | 2 | Cycle_wakeup_Node31 |  |  | uint16 | Read/Write
1302 | 1 | 2092 | 2 | Cycle_heathsta_Node31 |  |  | uint16 | Read/Write
1303 | 1 | 2094 | 2 | Data_numblock_Node31 |  |  | uint16 | Read/Write
1304 | 1 | 2096 | 2 | Data_reg 1_Node31 |  |  | uint16 | Read/Write
1305 | 1 | 2098 | 2 | Data_numreg 1_Node31 |  |  | uint16 | Read/Write
1306 | 1 | 2100 | 2 | Data_reg 2_Node31 |  |  | uint16 | Read/Write
1307 | 1 | 2102 | 2 | Data_numReg 2_Node31 |  |  | uint16 | Read/Write
1308 | 1 | 2104 | 2 | Data_reg 3_Node31 |  |  | uint16 | Read/Write
1309 | 1 | 2106 | 2 | Data_numReg 3_Node31 |  |  | uint16 | Read/Write
1310 | 2 | 2108 | 4 | Delta_Differential Pressure_Node31 |  |  | float | Read/Write
1312 | 2 | 2112 | 4 | Offset_Differential Pressure_Node31 |  |  | float | Read/Write
1314 | 2 | 2116 | 4 | Offset_Temp_Node31 |  |  | float | Read/Write
1316 | 14 | 2120 | 28 | Reserve_regs_Node31 |  |  |  | Read/Write
1330 | 1 | 2148 | 2 | Update_enable_Node32 |  |  | hex | Read/Write
1331 | 1 | 2150 | 2 | Cycle_wakeup_Node32 |  |  | uint16 | Read/Write
1332 | 1 | 2152 | 2 | Cycle_heathsta_Node32 |  |  | uint16 | Read/Write
1333 | 1 | 2154 | 2 | Data_numblock_Node32 |  |  | uint16 | Read/Write
1334 | 1 | 2156 | 2 | Data_reg 1_Node32 |  |  | uint16 | Read/Write
1335 | 1 | 2158 | 2 | Data_numreg 1_Node32 |  |  | uint16 | Read/Write
1336 | 1 | 2160 | 2 | Data_reg 2_Node32 |  |  | uint16 | Read/Write
1337 | 1 | 2162 | 2 | Data_numReg 2_Node32 |  |  | uint16 | Read/Write
1338 | 1 | 2164 | 2 | Data_reg 3_Node32 |  |  | uint16 | Read/Write
1339 | 1 | 2166 | 2 | Data_numReg 3_Node32 |  |  | uint16 | Read/Write
1340 | 2 | 2168 | 4 | Delta_Differential Pressure_Node32 |  |  | float | Read/Write
1342 | 2 | 2172 | 4 | Offset_Differential Pressure_Node32 |  |  | float | Read/Write
1344 | 2 | 2176 | 4 | Offset_Temp_Node32 |  |  | float | Read/Write
1346 | 14 | 2180 | 28 | Reserve_regs_Node32 |  |  |  | Read/Write
1360 | 1 | 2208 | 2 | Update_enable_Node33 |  |  | hex | Read/Write
1361 | 1 | 2210 | 2 | Cycle_wakeup_Node33 |  |  | uint16 | Read/Write
1362 | 1 | 2212 | 2 | Cycle_heathsta_Node33 |  |  | uint16 | Read/Write
1363 | 1 | 2214 | 2 | Data_numblock_Node33 |  |  | uint16 | Read/Write
1364 | 1 | 2216 | 2 | Data_reg 1_Node33 |  |  | uint16 | Read/Write
1365 | 1 | 2218 | 2 | Data_numreg 1_Node33 |  |  | uint16 | Read/Write
1366 | 1 | 2220 | 2 | Data_reg 2_Node33 |  |  | uint16 | Read/Write
1367 | 1 | 2222 | 2 | Data_numReg 2_Node33 |  |  | uint16 | Read/Write
1368 | 1 | 2224 | 2 | Data_reg 3_Node33 |  |  | uint16 | Read/Write
1369 | 1 | 2226 | 2 | Data_numReg 3_Node33 |  |  | uint16 | Read/Write
1370 | 2 | 2228 | 4 | Delta_Differential Pressure_Node33 |  |  | float | Read/Write
1372 | 2 | 2232 | 4 | Offset_Differential Pressure_Node33 |  |  | float | Read/Write
1374 | 2 | 2236 | 4 | Offset_Temp_Node33 |  |  | float | Read/Write
1376 | 14 | 2240 | 28 | Reserve_regs_Node33 |  |  |  | Read/Write
1390 | 1 | 2268 | 2 | Update_enable_Node34 |  |  | hex | Read/Write
1391 | 1 | 2270 | 2 | Cycle_wakeup_Node34 |  |  | uint16 | Read/Write
1392 | 1 | 2272 | 2 | Cycle_heathsta_Node34 |  |  | uint16 | Read/Write
1393 | 1 | 2274 | 2 | Data_numblock_Node34 |  |  | uint16 | Read/Write
1394 | 1 | 2276 | 2 | Data_reg 1_Node34 |  |  | uint16 | Read/Write
1395 | 1 | 2278 | 2 | Data_numreg 1_Node34 |  |  | uint16 | Read/Write
1396 | 1 | 2280 | 2 | Data_reg 2_Node34 |  |  | uint16 | Read/Write
1397 | 1 | 2282 | 2 | Data_numReg 2_Node34 |  |  | uint16 | Read/Write
1398 | 1 | 2284 | 2 | Data_reg 3_Node34 |  |  | uint16 | Read/Write
1399 | 1 | 2286 | 2 | Data_numReg 3_Node34 |  |  | uint16 | Read/Write
1400 | 2 | 2288 | 4 | Delta_Differential Pressure_Node34 |  |  | float | Read/Write
1402 | 2 | 2292 | 4 | Offset_Differential Pressure_Node34 |  |  | float | Read/Write
1404 | 2 | 2296 | 4 | Offset_Temp_Node34 |  |  | float | Read/Write
1406 | 14 | 2300 | 28 | Reserve_regs_Node34 |  |  |  | Read/Write
1420 | 1 | 2328 | 2 | Update_enable_Node35 |  |  | hex | Read/Write
1421 | 1 | 2330 | 2 | Cycle_wakeup_Node35 |  |  | uint16 | Read/Write
1422 | 1 | 2332 | 2 | Cycle_heathsta_Node35 |  |  | uint16 | Read/Write
1423 | 1 | 2334 | 2 | Data_numblock_Node35 |  |  | uint16 | Read/Write
1424 | 1 | 2336 | 2 | Data_reg 1_Node35 |  |  | uint16 | Read/Write
1425 | 1 | 2338 | 2 | Data_numreg 1_Node35 |  |  | uint16 | Read/Write
1426 | 1 | 2340 | 2 | Data_reg 2_Node35 |  |  | uint16 | Read/Write
1427 | 1 | 2342 | 2 | Data_numReg 2_Node35 |  |  | uint16 | Read/Write
1428 | 1 | 2344 | 2 | Data_reg 3_Node35 |  |  | uint16 | Read/Write
1429 | 1 | 2346 | 2 | Data_numReg 3_Node35 |  |  | uint16 | Read/Write
1430 | 2 | 2348 | 4 | Delta_Differential Pressure_Node35 |  |  | float | Read/Write
1432 | 2 | 2352 | 4 | Offset_Differential Pressure_Node35 |  |  | float | Read/Write
1434 | 2 | 2356 | 4 | Offset_Temp_Node35 |  |  | float | Read/Write
1436 | 14 | 2360 | 28 | Reserve_regs_Node35 |  |  |  | Read/Write
1450 | 1 | 2388 | 2 | Update_enable_Node36 |  |  | hex | Read/Write
1451 | 1 | 2390 | 2 | Cycle_wakeup_Node36 |  |  | uint16 | Read/Write
1452 | 1 | 2392 | 2 | Cycle_heathsta_Node36 |  |  | uint16 | Read/Write
1453 | 1 | 2394 | 2 | Data_numblock_Node36 |  |  | uint16 | Read/Write
1454 | 1 | 2396 | 2 | Data_reg 1_Node36 |  |  | uint16 | Read/Write
1455 | 1 | 2398 | 2 | Data_numreg 1_Node36 |  |  | uint16 | Read/Write
1456 | 1 | 2400 | 2 | Data_reg 2_Node36 |  |  | uint16 | Read/Write
1457 | 1 | 2402 | 2 | Data_numReg 2_Node36 |  |  | uint16 | Read/Write
1458 | 1 | 2404 | 2 | Data_reg 3_Node36 |  |  | uint16 | Read/Write
1459 | 1 | 2406 | 2 | Data_numReg 3_Node36 |  |  | uint16 | Read/Write
1460 | 2 | 2408 | 4 | Delta_Differential Pressure_Node36 |  |  | float | Read/Write
1462 | 2 | 2412 | 4 | Offset_Differential Pressure_Node36 |  |  | float | Read/Write
1464 | 2 | 2416 | 4 | Offset_Temp_Node36 |  |  | float | Read/Write
1466 | 14 | 2420 | 28 | Reserve_regs_Node36 |  |  |  | Read/Write
1480 | 1 | 2448 | 2 | Update_enable_Node37 |  |  | hex | Read/Write
1481 | 1 | 2450 | 2 | Cycle_wakeup_Node37 |  |  | uint16 | Read/Write
1482 | 1 | 2452 | 2 | Cycle_heathsta_Node37 |  |  | uint16 | Read/Write
1483 | 1 | 2454 | 2 | Data_numblock_Node37 |  |  | uint16 | Read/Write
1484 | 1 | 2456 | 2 | Data_reg 1_Node37 |  |  | uint16 | Read/Write
1485 | 1 | 2458 | 2 | Data_numreg 1_Node37 |  |  | uint16 | Read/Write
1486 | 1 | 2460 | 2 | Data_reg 2_Node37 |  |  | uint16 | Read/Write
1487 | 1 | 2462 | 2 | Data_numReg 2_Node37 |  |  | uint16 | Read/Write
1488 | 1 | 2464 | 2 | Data_reg 3_Node37 |  |  | uint16 | Read/Write
1489 | 1 | 2466 | 2 | Data_numReg 3_Node37 |  |  | uint16 | Read/Write
1490 | 2 | 2468 | 4 | Delta_Differential Pressure_Node37 |  |  | float | Read/Write
1492 | 2 | 2472 | 4 | Offset_Differential Pressure_Node37 |  |  | float | Read/Write
1494 | 2 | 2476 | 4 | Offset_Temp_Node37 |  |  | float | Read/Write
1496 | 14 | 2480 | 28 | Reserve_regs_Node37 |  |  |  | Read/Write
1510 | 1 | 2508 | 2 | Update_enable_Node38 |  |  | hex | Read/Write
1511 | 1 | 2510 | 2 | Cycle_wakeup_Node38 |  |  | uint16 | Read/Write
1512 | 1 | 2512 | 2 | Cycle_heathsta_Node38 |  |  | uint16 | Read/Write
1513 | 1 | 2514 | 2 | Data_numblock_Node38 |  |  | uint16 | Read/Write
1514 | 1 | 2516 | 2 | Data_reg 1_Node38 |  |  | uint16 | Read/Write
1515 | 1 | 2518 | 2 | Data_numreg 1_Node38 |  |  | uint16 | Read/Write
1516 | 1 | 2520 | 2 | Data_reg 2_Node38 |  |  | uint16 | Read/Write
1517 | 1 | 2522 | 2 | Data_numReg 2_Node38 |  |  | uint16 | Read/Write
1518 | 1 | 2524 | 2 | Data_reg 3_Node38 |  |  | uint16 | Read/Write
1519 | 1 | 2526 | 2 | Data_numReg 3_Node38 |  |  | uint16 | Read/Write
1520 | 2 | 2528 | 4 | Delta_Differential Pressure_Node38 |  |  | float | Read/Write
1522 | 2 | 2532 | 4 | Offset_Differential Pressure_Node38 |  |  | float | Read/Write
1524 | 2 | 2536 | 4 | Offset_Temp_Node38 |  |  | float | Read/Write
1526 | 14 | 2540 | 28 | Reserve_regs_Node38 |  |  |  | Read/Write
1540 | 1 | 2568 | 2 | Update_enable_Node39 |  |  | hex | Read/Write
1541 | 1 | 2570 | 2 | Cycle_wakeup_Node39 |  |  | uint16 | Read/Write
1542 | 1 | 2572 | 2 | Cycle_heathsta_Node39 |  |  | uint16 | Read/Write
1543 | 1 | 2574 | 2 | Data_numblock_Node39 |  |  | uint16 | Read/Write
1544 | 1 | 2576 | 2 | Data_reg 1_Node39 |  |  | uint16 | Read/Write
1545 | 1 | 2578 | 2 | Data_numreg 1_Node39 |  |  | uint16 | Read/Write
1546 | 1 | 2580 | 2 | Data_reg 2_Node39 |  |  | uint16 | Read/Write
1547 | 1 | 2582 | 2 | Data_numReg 2_Node39 |  |  | uint16 | Read/Write
1548 | 1 | 2584 | 2 | Data_reg 3_Node39 |  |  | uint16 | Read/Write
1549 | 1 | 2586 | 2 | Data_numReg 3_Node39 |  |  | uint16 | Read/Write
1550 | 2 | 2588 | 4 | Delta_Differential Pressure_Node39 |  |  | float | Read/Write
1552 | 2 | 2592 | 4 | Offset_Differential Pressure_Node39 |  |  | float | Read/Write
1554 | 2 | 2596 | 4 | Offset_Temp_Node39 |  |  | float | Read/Write
1556 | 14 | 2600 | 28 | Reserve_regs_Node39 |  |  |  | Read/Write
1570 | 1 | 2628 | 2 | Update_enable_Node40 |  |  | hex | Read/Write
1571 | 1 | 2630 | 2 | Cycle_wakeup_Node40 |  |  | uint16 | Read/Write
1572 | 1 | 2632 | 2 | Cycle_heathsta_Node40 |  |  | uint16 | Read/Write
1573 | 1 | 2634 | 2 | Data_numblock_Node40 |  |  | uint16 | Read/Write
1574 | 1 | 2636 | 2 | Data_reg 1_Node40 |  |  | uint16 | Read/Write
1575 | 1 | 2638 | 2 | Data_numreg 1_Node40 |  |  | uint16 | Read/Write
1576 | 1 | 2640 | 2 | Data_reg 2_Node40 |  |  | uint16 | Read/Write
1577 | 1 | 2642 | 2 | Data_numReg 2_Node40 |  |  | uint16 | Read/Write
1578 | 1 | 2644 | 2 | Data_reg 3_Node40 |  |  | uint16 | Read/Write
1579 | 1 | 2646 | 2 | Data_numReg 3_Node40 |  |  | uint16 | Read/Write
1580 | 2 | 2648 | 4 | Delta_Differential Pressure_Node40 |  |  | float | Read/Write
1582 | 2 | 2652 | 4 | Offset_Differential Pressure_Node40 |  |  | float | Read/Write
1584 | 2 | 2656 | 4 | Offset_Temp_Node40 |  |  | float | Read/Write
1586 | 14 | 2660 | 28 | Reserve_regs_Node40 |  |  |  | Read/Write