## Memmap of WS433-CL V2.0
MODBUS MEMORY MAP of WS433-CL Version 2.0
For Simple operation, just set up the "ADDING WIRELESS SENSORS"
| (1) | (2) | (3) | (4) |  | (5) |  | (6) | (7) | (8) | (9) | (10) | (11) | (12)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of Register | Adr | Byte Size | Description | Range | Default | Format | Property | Comment
ADDING WIRELESS SENSORS | 40273 | 272 | 110 | 3 | 16 | 1 | 32 | 2 | Num of Node |  | 0 | uint16 | Read/Write | Write "num of node" = 0 => allow deleting to all node-id of co-ordinator
| 40274 | 273 | 111 | 3 | 16 | 2 | 34 | 4 | Node id 1 |  | 0 | uint32 | Read/Write | Config the ID number of each wireless sensor (the last 9 digits of sensor's S/N)
| 40276 | 275 | 113 | 3 | 16 | 2 | 38 | 4 | Node id 2 |  | 0 | uint32 | Read/Write
| 40278 | 277 | 115 | 3 | 16 | 2 | 42 | 4 | Node id 3 |  | 0 | uint32 | Read/Write
| 40280 | 279 | 117 | 3 | 16 | 2 | 46 | 4 | Node id 4 |  | 0 | uint32 | Read/Write
| 40282 | 281 | 119 | 3 | 16 | 2 | 50 | 4 | Node id 5 |  | 0 | uint32 | Read/Write
| 40284 | 283 | 11B | 3 | 16 | 2 | 54 | 4 | Node id 6 |  | 0 | uint32 | Read/Write
| 40286 | 285 | 11D | 3 | 16 | 2 | 58 | 4 | Node id 7 |  | 0 | uint32 | Read/Write
| 40288 | 287 | 11F | 3 | 16 | 2 | 62 | 4 | Node id 8 |  | 0 | uint32 | Read/Write
| 40290 | 289 | 121 | 3 | 16 | 2 | 66 | 4 | Node id 9 |  | 0 | uint32 | Read/Write
| 40292 | 291 | 123 | 3 | 16 | 2 | 70 | 4 | Node id 10 |  | 0 | uint32 | Read/Write
| 40294 | 293 | 125 | 3 | 16 | 2 | 74 | 4 | Node id 11 |  | 0 | uint32 | Read/Write
| 40296 | 295 | 127 | 3 | 16 | 2 | 78 | 4 | Node id 12 |  | 0 | uint32 | Read/Write
| 40298 | 297 | 129 | 3 | 16 | 2 | 82 | 4 | Node id 13 |  | 0 | uint32 | Read/Write
| 40300 | 299 | 12B | 3 | 16 | 2 | 86 | 4 | Node id 14 |  | 0 | uint32 | Read/Write
| 40302 | 301 | 12D | 3 | 16 | 2 | 90 | 4 | Node id 15 |  | 0 | uint32 | Read/Write
| 40304 | 303 | 12F | 3 | 16 | 2 | 94 | 4 | Node id 16 |  | 0 | uint32 | Read/Write
| 40306 | 305 | 131 | 3 | 16 | 2 | 98 | 4 | Node id 17 |  | 0 | uint32 | Read/Write
| 40308 | 307 | 133 | 3 | 16 | 2 | 102 | 4 | Node id 18 |  | 0 | uint32 | Read/Write
| 40310 | 309 | 135 | 3 | 16 | 2 | 106 | 4 | Node id 19 |  | 0 | uint32 | Read/Write
| 40312 | 311 | 137 | 3 | 16 | 2 | 110 | 4 | Node id 20 |  | 0 | uint32 | Read/Write
| 40314 | 313 | 139 | 3 | 16 | 2 | 114 | 4 | Node id 21 |  | 0 | uint32 | Read/Write
| 40316 | 315 | 13B | 3 | 16 | 2 | 118 | 4 | Node id 22 |  | 0 | uint32 | Read/Write
| 40318 | 317 | 13D | 3 | 16 | 2 | 122 | 4 | Node id 23 |  | 0 | uint32 | Read/Write
| 40320 | 319 | 13F | 3 | 16 | 2 | 126 | 4 | Node id 24 |  | 0 | uint32 | Read/Write
| 40322 | 321 | 141 | 3 | 16 | 2 | 130 | 4 | Node id 25 |  | 0 | uint32 | Read/Write
| 40324 | 323 | 143 | 3 | 16 | 2 | 134 | 4 | Node id 26 |  | 0 | uint32 | Read/Write
| 40326 | 325 | 145 | 3 | 16 | 2 | 138 | 4 | Node id 27 |  | 0 | uint32 | Read/Write
| 40328 | 327 | 147 | 3 | 16 | 2 | 142 | 4 | Node id 28 |  | 0 | uint32 | Read/Write
| 40330 | 329 | 149 | 3 | 16 | 2 | 146 | 4 | Node id 29 |  | 0 | uint32 | Read/Write
| 40332 | 331 | 14B | 3 | 16 | 2 | 150 | 4 | Node id 30 |  | 0 | uint32 | Read/Write
| 40334 | 333 | 14D | 3 | 16 | 2 | 154 | 4 | Node id 31 |  | 0 | uint32 | Read/Write
| 40336 | 335 | 14F | 3 | 16 | 2 | 158 | 4 | Node id 32 |  | 0 | uint32 | Read/Write
| 40338 | 337 | 151 | 3 | 16 | 2 | 162 | 4 | Node id 33 |  | 0 | uint32 | Read/Write
| 40340 | 339 | 153 | 3 | 16 | 2 | 166 | 4 | Node id 34 |  | 0 | uint32 | Read/Write
| 40342 | 341 | 155 | 3 | 16 | 2 | 170 | 4 | Node id 35 |  | 0 | uint32 | Read/Write
| 40344 | 343 | 157 | 3 | 16 | 2 | 174 | 4 | Node id 36 |  | 0 | uint32 | Read/Write
| 40346 | 345 | 159 | 3 | 16 | 2 | 178 | 4 | Node id 37 |  | 0 | uint32 | Read/Write
| 40348 | 347 | 15B | 3 | 16 | 2 | 182 | 4 | Node id 38 |  | 0 | uint32 | Read/Write
| 40350 | 349 | 15D | 3 | 16 | 2 | 186 | 4 | Node id 39 |  | 0 | uint32 | Read/Write
| 40352 | 351 | 15F | 3 | 16 | 2 | 190 | 4 | Node id 40 |  | 0 | uint32 | Read/Write
MODBUS PORT CONFIG | 40257 | 256 | 100 | 3 | 16 | 1 | 0 | 2 | Modbus address | 1-247 | 1 | uint16 | Read/Write
| 40258 | 257 | 101 | 3 | 16 | 1 | 2 | 2 | Modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
| 40259 | 258 | 102 | 3 | 16 | 1 | 4 | 2 | Modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
OPERATION DATA OF 40 WIRELESS SENSORS | 30001 | 0 | 0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 1; (11): Read; (12): Details in sheet of sensor
| 30033 | 32 | 20 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 2; (11): Read
| 30065 | 64 | 40 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 3; (11): Read
| 30097 | 96 | 60 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 4; (11): Read
| 30129 | 128 | 80 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 5; (11): Read
| 30161 | 160 | A0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 6; (11): Read
| 30193 | 192 | C0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 7; (11): Read
| 30225 | 224 | E0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 8; (11): Read
| 30257 | 256 | 100 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 9; (11): Read
| 30289 | 288 | 120 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 10; (11): Read
| 30321 | 320 | 140 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 11; (11): Read
| 30353 | 352 | 160 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 12; (11): Read
| 30385 | 384 | 180 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 13; (11): Read
| 30417 | 416 | 1A0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 14; (11): Read
| 30449 | 448 | 1C0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 15; (11): Read
| 30481 | 480 | 1E0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 16; (11): Read
| 30513 | 512 | 200 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 17; (11): Read
| 30545 | 544 | 220 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 18; (11): Read
| 30577 | 576 | 240 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 19; (11): Read
| 30609 | 608 | 260 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 20; (11): Read
| 30641 | 640 | 280 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 21; (11): Read
| 30673 | 672 | 2A0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 22; (11): Read
| 30705 | 704 | 2C0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 23; (11): Read
| 30737 | 736 | 2E0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 24; (11): Read
| 30769 | 768 | 300 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 25; (11): Read
| 30801 | 800 | 320 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 26; (11): Read
| 30833 | 832 | 340 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 27; (11): Read
| 30865 | 864 | 360 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 28; (11): Read
| 30897 | 896 | 380 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 29; (11): Read
| 30929 | 928 | 3A0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 30; (11): Read
| 30961 | 960 | 3C0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 31; (11): Read
| 30993 | 992 | 3E0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 32; (11): Read
| 31025 | 1024 | 400 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 33; (11): Read
| 31057 | 1056 | 420 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 34; (11): Read
| 31089 | 1088 | 440 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 35; (11): Read
| 31121 | 1120 | 460 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 36; (11): Read
| 31153 | 1152 | 480 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 37; (11): Read
| 31185 | 1184 | 4A0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 38; (11): Read
| 31217 | 1216 | 4C0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 39; (11): Read
| 31249 | 1248 | 4E0 | 4 |  | 32 |  | (6): 64; (7): Data area of Node 40; (11): Read
OPERATION DATA OF 40 WIRELESS SENSORS FOR ICONNECTOR (*) | 81217 | 41216 | A100 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 1; (11): Read; (12): Details in sheet of sensor
| 81473 | 41472 | A200 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 2; (11): Read
| 81729 | 41728 | A300 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 3; (11): Read
| 81985 | 41984 | A400 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 4; (11): Read
| 82241 | 42240 | A500 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 5; (11): Read
| 82497 | 42496 | A600 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 6; (11): Read
| 82753 | 42752 | A700 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 7; (11): Read
| 83009 | 43008 | A800 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 8; (11): Read
| 83265 | 43264 | A900 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 9; (11): Read
| 83521 | 43520 | AA00 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 10; (11): Read
| 85313 | 45312 | B100 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 11; (11): Read
| 85569 | 45568 | B200 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 12; (11): Read
| 85825 | 45824 | B300 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 13; (11): Read
| 86081 | 46080 | B400 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 14; (11): Read
| 86337 | 46336 | B500 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 15; (11): Read
| 86593 | 46592 | B600 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 16; (11): Read
| 86849 | 46848 | B700 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 17; (11): Read
| 87105 | 47104 | B800 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 18; (11): Read
| 87361 | 47360 | B900 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 19; (11): Read
| 87617 | 47616 | BA00 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 20; (11): Read
| 89409 | 49408 | C100 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 21; (11): Read
| 89665 | 49664 | C200 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 22; (11): Read
| 89921 | 49920 | C300 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 23; (11): Read
| 90177 | 50176 | C400 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 24; (11): Read
| 90433 | 50432 | C500 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 25; (11): Read
| 90689 | 50688 | C600 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 26; (11): Read
| 90945 | 50944 | C700 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 27; (11): Read
| 91201 | 51200 | C800 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 28; (11): Read
| 91457 | 51456 | C900 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 29; (11): Read
| 91713 | 51712 | CA00 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 30; (11): Read
| 93505 | 53504 | D100 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 31; (11): Read
| 93761 | 53760 | D200 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 32; (11): Read
| 94017 | 54016 | D300 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 33; (11): Read
| 94273 | 54272 | D400 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 34; (11): Read
| 94529 | 54528 | D500 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 35; (11): Read
| 94785 | 54784 | D600 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 36; (11): Read
| 95041 | 55040 | D700 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 37; (11): Read
| 95297 | 55296 | D800 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 38; (11): Read
| 95553 | 55552 | D900 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 39; (11): Read
| 95809 | 55808 | DA00 | 3 |  | 256 |  | (6): 512; (7): Data area of Node 40; (11): Read
STATUS DATA OF 40 WIRELESS SENSORS | 40009 | 8 | 8 | 3 |  | 20 | 16 | 40 | Rssi node 1..40 |  |  | byte | Read | Only for manuafacture. Raw RSSI value (right number must subtract 256, Unit is dBm).
| 40029 | 28 | 1C | 3 |  | 1 | 56 | 2 | Data status node 1 & Data status node 2 | 0-9, 99 |  | byte | Read | Hi-byte for node 1 & lo-byte for node 2. Details in sheet of sensor
| 40030 | 29 | 1D | 3 |  | 1 | 58 | 2 | Data status node 3 & Data status node 4 | 0-9, 99 |  | byte | Read
| 40031 | 30 | 1E | 3 |  | 1 | 60 | 2 | Data status node 5 & Data status node 6 | 0-9, 99 |  | byte | Read
| 40032 | 31 | 1F | 3 |  | 1 | 62 | 2 | Data status node 7 & Data status node 8 | 0-9, 99 |  | byte | Read
| 40033 | 32 | 20 | 3 |  | 1 | 64 | 2 | Data status node 9 & Data status node 10 | 0-9, 99 |  | byte | Read
| 40034 | 33 | 21 | 3 |  | 1 | 66 | 2 | Data status node 11 & Data status node 12 | 0-9, 99 |  | byte | Read
| 40035 | 34 | 22 | 3 |  | 1 | 68 | 2 | Data status node 13 & Data status node 14 | 0-9, 99 |  | byte | Read
| 40036 | 35 | 23 | 3 |  | 1 | 70 | 2 | Data status node 15 & Data status node 16 | 0-9, 99 |  | byte | Read
| 40037 | 36 | 24 | 3 |  | 1 | 72 | 2 | Data status node 17 & Data status node 18 | 0-9, 99 |  | byte | Read
| 40038 | 37 | 25 | 3 |  | 1 | 74 | 2 | Data status node 19 & Data status node 20 | 0-9, 99 |  | byte | Read
| 40039 | 38 | 26 | 3 |  | 1 | 76 | 2 | Data status node 21 & Data status node 22 | 0-9, 99 |  | byte | Read
| 40040 | 39 | 27 | 3 |  | 1 | 78 | 2 | Data status node 23 & Data status node 24 | 0-9, 99 |  | byte | Read
| 40041 | 40 | 28 | 3 |  | 1 | 80 | 2 | Data status node 25 & Data status node 26 | 0-9, 99 |  | byte | Read
| 40042 | 41 | 29 | 3 |  | 1 | 82 | 2 | Data status node 27 & Data status node 28 | 0-9, 99 |  | byte | Read
| 40043 | 42 | 2A | 3 |  | 1 | 84 | 2 | Data status node 29 & Data status node 30 | 0-9, 99 |  | byte | Read
| 40044 | 43 | 2B | 3 |  | 1 | 86 | 2 | Data status node 31 & Data status node 32 | 0-9, 99 |  | byte | Read
| 40045 | 44 | 2C | 3 |  | 1 | 88 | 2 | Data status node 33 & Data status node 34 | 0-9, 99 |  | byte | Read
| 40046 | 45 | 2D | 3 |  | 1 | 90 | 2 | Data status node 35 & Data status node 36 | 0-9, 99 |  | byte | Read
| 40047 | 46 | 2E | 3 |  | 1 | 92 | 2 | Data status node 37 & Data status node 38 | 0-9, 99 |  | byte | Read
| 40048 | 47 | 2F | 3 |  | 1 | 94 | 2 | Data status node 39 & Data status node 40 | 0-9, 99 |  | byte | Read
| 40049 | 48 | 30 | 3 |  | 20 | 96 | 40 | RF timeout count node 1..40 | 0-255 |  | byte | Read | Counting the number of times that no data from wireless sensor arrived over "timeout_count_threshold" seconds , for ADVANCED diagnostic the RF connection between wireless sensor and co-ordinator
| 40069 | 68 | 44 | 3 |  | 1 | 136 | 2 | RF signal strength of node 1 & RF signal strength of node 2 | 0-4 |  | byte | Read | Hi-byte for node 1 & lo-byte for node 2. Details in sheet of sensor
| 40070 | 69 | 45 | 3 |  | 1 | 138 | 2 | RF signal strength of node 3 & RF signal strength of node 4 | 0-4 |  | byte | Read
| 40071 | 70 | 46 | 3 |  | 1 | 140 | 2 | RF signal strength of node 5 & RF signal strength of node 6 | 0-4 |  | byte | Read
| 40072 | 71 | 47 | 3 |  | 1 | 142 | 2 | RF signal strength of node 7 & RF signal strength of node 8 | 0-4 |  | byte | Read
| 40073 | 72 | 48 | 3 |  | 1 | 144 | 2 | RF signal strength of node 9 & RF signal strength of node 10 | 0-4 |  | byte | Read
| 40074 | 73 | 49 | 3 |  | 1 | 146 | 2 | RF signal strength of node 11 & RF signal strength of node 12 | 0-4 |  | byte | Read
| 40075 | 74 | 4A | 3 |  | 1 | 148 | 2 | RF signal strength of node 13 & RF signal strength of node 14 | 0-4 |  | byte | Read
| 40076 | 75 | 4B | 3 |  | 1 | 150 | 2 | RF signal strength of node 15 & RF signal strength of node 16 | 0-4 |  | byte | Read
| 40077 | 76 | 4C | 3 |  | 1 | 152 | 2 | RF signal strength of node 17 & RF signal strength of node 18 | 0-4 |  | byte | Read
| 40078 | 77 | 4D | 3 |  | 1 | 154 | 2 | RF signal strength of node 19 & RF signal strength of node 20 | 0-4 |  | byte | Read
| 40079 | 78 | 4E | 3 |  | 1 | 156 | 2 | RF signal strength of node 21 & RF signal strength of node 22 | 0-4 |  | byte | Read
| 40080 | 79 | 4F | 3 |  | 1 | 158 | 2 | RF signal strength of node 23 & RF signal strength of node 24 | 0-4 |  | byte | Read
| 40081 | 80 | 50 | 3 |  | 1 | 160 | 2 | RF signal strength of node 25 & RF signal strength of node 26 | 0-4 |  | byte | Read
| 40082 | 81 | 51 | 3 |  | 1 | 162 | 2 | RF signal strength of node 27 & RF signal strength of node 28 | 0-4 |  | byte | Read
| 40083 | 82 | 52 | 3 |  | 1 | 164 | 2 | RF signal strength of node 29 & RF signal strength of node 30 | 0-4 |  | byte | Read
| 40084 | 83 | 53 | 3 |  | 1 | 166 | 2 | RF signal strength of node 31 & RF signal strength of node 32 | 0-4 |  | byte | Read
| 40085 | 84 | 54 | 3 |  | 1 | 168 | 2 | RF signal strength of node 33 & RF signal strength of node 34 | 0-4 |  | byte | Read
| 40086 | 85 | 55 | 3 |  | 1 | 170 | 2 | RF signal strength of node 35 & RF signal strength of node 36 | 0-4 |  | byte | Read
| 40087 | 86 | 56 | 3 |  | 1 | 172 | 2 | RF signal strength of node 37 & RF signal strength of node 38 | 0-4 |  | byte | Read
| 40088 | 87 | 57 | 3 |  | 1 | 174 | 2 | RF signal strength of node 39 & RF signal strength of node 40 | 0-4 |  | byte | Read
| 40089 | 88 | 58 | 3 |  | 60 | 176 | (6): 120; (7): spare; (10): byte; (11): Read
| 40149 | 148 | 94 | 3 |  | 20 | 296 | 40 | Rx seq node 1..40 | 0-255 |  | byte | Read | Only for manuafacture. Sequence number of data package, value from wireless sensor, for ADVANCED diagnostic of RF connecttion, to know lost of data package from sensor to Co-ordinator
| 40169 | 168 | A8 | 3 |  | 20 | 336 | 40 | Rx duplication count node 1..40 | 0-255 |  | byte | Read | For manuafacture. Counting the number of Dupplicated data package from sensor, to define that sensor have not received the ACK package from Co-ordinator
| 40189 | 188 | BC | 3 |  | 1 | 376 | 2 | Sync status node 1 & Sync status node 2 | 0, 1, 99 |  | byte | Read | Hi-byte for node 1 & lo-byte for node 2. Details in sheet of sensor
| 40190 | 189 | BD | 3 |  | 1 | 378 | 2 | Sync status node 3 & Sync status node 4 | 0, 1, 99 |  | byte | Read
| 40191 | 190 | BE | 3 |  | 1 | 380 | 2 | Sync status node 5 & Sync status node 6 | 0, 1, 99 |  | byte | Read
| 40192 | 191 | BF | 3 |  | 1 | 382 | 2 | Sync status node 7 & Sync status node 8 | 0, 1, 99 |  | byte | Read
| 40193 | 192 | C0 | 3 |  | 1 | 384 | 2 | Sync status node 9 & Sync status node 10 | 0, 1, 99 |  | byte | Read
| 40194 | 193 | C1 | 3 |  | 1 | 386 | 2 | Sync status node 11 & Sync status node 12 | 0, 1, 99 |  | byte | Read
| 40195 | 194 | C2 | 3 |  | 1 | 388 | 2 | Sync status node 13 & Sync status node 14 | 0, 1, 99 |  | byte | Read
| 40196 | 195 | C3 | 3 |  | 1 | 390 | 2 | Sync status node 15 & Sync status node 16 | 0, 1, 99 |  | byte | Read
| 40197 | 196 | C4 | 3 |  | 1 | 392 | 2 | Sync status node 17 & Sync status node 18 | 0, 1, 99 |  | byte | Read
| 40198 | 197 | C5 | 3 |  | 1 | 394 | 2 | Sync status node 19 & Sync status node 20 | 0, 1, 99 |  | byte | Read
| 40199 | 198 | C6 | 3 |  | 1 | 396 | 2 | Sync status node 21 & Sync status node 22 | 0, 1, 99 |  | byte | Read
| 40200 | 199 | C7 | 3 |  | 1 | 398 | 2 | Sync status node 23 & Sync status node 24 | 0, 1, 99 |  | byte | Read
| 40201 | 200 | C8 | 3 |  | 1 | 400 | 2 | Sync status node 25 & Sync status node 26 | 0, 1, 99 |  | byte | Read
| 40202 | 201 | C9 | 3 |  | 1 | 402 | 2 | Sync status node 27 & Sync status node 28 | 0, 1, 99 |  | byte | Read
| 40203 | 202 | CA | 3 |  | 1 | 404 | 2 | Sync status node 29 & Sync status node 30 | 0, 1, 99 |  | byte | Read
| 40204 | 203 | CB | 3 |  | 1 | 406 | 2 | Sync status node 31 & Sync status node 32 | 0, 1, 99 |  | byte | Read
| 40205 | 204 | CC | 3 |  | 1 | 408 | 2 | Sync status node 33 & Sync status node 34 | 0, 1, 99 |  | byte | Read
| 40206 | 205 | CD | 3 |  | 1 | 410 | 2 | Sync status node 35 & Sync status node 36 | 0, 1, 99 |  | byte | Read
| 40207 | 206 | CE | 3 |  | 1 | 412 | 2 | Sync status node 37 & Sync status node 38 | 0, 1, 99 |  | byte | Read
| 40208 | 207 | CF | 3 |  | 1 | 414 | 2 | Sync status node 39 & Sync status node 40 | 0, 1, 99 |  | byte | Read
STATUS DATA OF TRAILER TRACKING | 40209 | 210 | D2 | 3 |  | 2 | 416 | (6): 4; (7): Trailer: ID Sensor Tag; (10): uint32; (11): Read
| 40211 | 212 | D4 | 3 |  | 1 | 420 | (6): 2; (7): Trailer: % Battery of Sensor Tag; (10): uint16; (11): Read
| 40212 | 213 | D5 | 3 |  | 1 | 422 | (6): 2; (7): Trailer: RF signal strength + error code; (10): uint8; (11): Read
| 40212 | 214 | D6 | 3 |  | 1 | 422 | (6): 2; (7): Trailer: RF rssi; (10): int16; (11): Read
| 40211 | 215 | D7 | 3 |  | 1 | 420 | (6): 2; (7): Last RF rssi; (10): int16; (11): Read
| 40209 | 216 | D8 | 3 |  | 2 | 416 | (6): 4; (7): Last ID Sensor Tag; (10): int32; (11): Read
CONTROL DATA OF 40 WIRELESS SENSORS | 42001 | 2000 | 7D0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 1; (11): Read/Write; (12): Control area for each wireless sensor, see details in sheet of sensor
| 42009 | 2008 | 7D8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 2; (11): Read/Write
| 42017 | 2016 | 7E0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 3; (11): Read/Write
| 42025 | 2024 | 7E8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 4; (11): Read/Write
| 42033 | 2032 | 7F0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 5; (11): Read/Write
| 42041 | 2040 | 7F8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 6; (11): Read/Write
| 42049 | 2048 | 800 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 7; (11): Read/Write
| 42057 | 2056 | 808 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 8; (11): Read/Write
| 42065 | 2064 | 810 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 9; (11): Read/Write
| 42073 | 2072 | 818 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 10; (11): Read/Write
| 42081 | 2080 | 820 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 11; (11): Read/Write
| 42089 | 2088 | 828 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 12; (11): Read/Write
| 42097 | 2096 | 830 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 13; (11): Read/Write
| 42105 | 2104 | 838 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 14; (11): Read/Write
| 42113 | 2112 | 840 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 15; (11): Read/Write
| 42121 | 2120 | 848 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 16; (11): Read/Write
| 42129 | 2128 | 850 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 17; (11): Read/Write
| 42137 | 2136 | 858 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 18; (11): Read/Write
| 42145 | 2144 | 860 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 19; (11): Read/Write
| 42153 | 2152 | 868 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 20; (11): Read/Write
| 42161 | 2160 | 870 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 21; (11): Read/Write
| 42169 | 2168 | 878 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 22; (11): Read/Write
| 42177 | 2176 | 880 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 23; (11): Read/Write
| 42185 | 2184 | 888 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 24; (11): Read/Write
| 42193 | 2192 | 890 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 25; (11): Read/Write
| 42201 | 2200 | 898 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 26; (11): Read/Write
| 42209 | 2208 | 8A0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 27; (11): Read/Write
| 42217 | 2216 | 8A8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 28; (11): Read/Write
| 42225 | 2224 | 8B0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 29; (11): Read/Write
| 42233 | 2232 | 8B8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 30; (11): Read/Write
| 42241 | 2240 | 8C0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 31; (11): Read/Write
| 42249 | 2248 | 8C8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 32; (11): Read/Write
| 42257 | 2256 | 8D0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 33; (11): Read/Write
| 42265 | 2264 | 8D8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 34; (11): Read/Write
| 42273 | 2272 | 8E0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 35; (11): Read/Write
| 42281 | 2280 | 8E8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 36; (11): Read/Write
| 42289 | 2288 | 8F0 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 37; (11): Read/Write
| 42297 | 2296 | 8F8 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 38; (11): Read/Write
| 42305 | 2304 | 900 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 39; (11): Read/Write
| 42313 | 2312 | 908 | 3 | 16 | 8 |  | (6): 16; (7): Control area of node 40; (11): Read/Write
SYSTEM CONFIG | 40260 | 259 | 103 | 3 | 16 | 9 | 6 | 18 | Serial number |  |  | string | Read/Write(PW) | Only for manuafacture. Serial number of Wireless sensor co-ordinator.
| 40269 | 268 | 10C | 3 | 16 | 2 | 24 | 4 | Password for setting |  |  | uint32 | Read/Write | Password for writing co-ordinator S/N and ID.
| 40271 | 270 | 10E | 3 | 16 | 2 | 28 | 4 | Co-ordinator id |  |  | uint32 | Read/Write(PW) | Only for manuafacture. The ID number of Wireless sensor co-ordinator.
ADVANCED CONFIG | 40401 | 400 | 190 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 1; (11): Read/Write; (12): Configuration data area for each wireless sensor, see details in sheet of sensor
| 40441 | 440 | 1B8 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 2; (11): Read/Write
| 40481 | 480 | 1E0 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 3; (11): Read/Write
| 40521 | 520 | 208 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 4; (11): Read/Write
| 40561 | 560 | 230 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 5; (11): Read/Write
| 40601 | 600 | 258 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 6; (11): Read/Write
| 40641 | 640 | 280 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 7; (11): Read/Write
| 40681 | 680 | 2A8 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 8; (11): Read/Write
| 40721 | 720 | 2D0 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 9; (11): Read/Write
| 40761 | 760 | 2F8 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 10; (11): Read/Write
| 40801 | 800 | 320 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 11; (11): Read/Write
| 40841 | 840 | 348 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 12; (11): Read/Write
| 40881 | 880 | 370 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 13; (11): Read/Write
| 40921 | 920 | 398 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 14; (11): Read/Write
| 40961 | 960 | 3C0 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 15; (11): Read/Write
| 41001 | 1000 | 3E8 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 16; (11): Read/Write
| 41041 | 1040 | 410 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 17; (11): Read/Write
| 41081 | 1080 | 438 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 18; (11): Read/Write
| 41121 | 1120 | 460 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 19; (11): Read/Write
| 41161 | 1160 | 488 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 20; (11): Read/Write
| 41201 | 1200 | 4B0 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 21; (11): Read/Write
| 41241 | 1240 | 4D8 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 22; (11): Read/Write
| 41281 | 1280 | 500 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 23; (11): Read/Write
| 41321 | 1320 | 528 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 24; (11): Read/Write
| 41361 | 1360 | 550 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 25; (11): Read/Write
| 41401 | 1400 | 578 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 26; (11): Read/Write
| 41441 | 1440 | 5A0 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 27; (11): Read/Write
| 41481 | 1480 | 5C8 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 28; (11): Read/Write
| 41521 | 1520 | 5F0 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 29; (11): Read/Write
| 41561 | 1560 | 618 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 30; (11): Read/Write
| 41601 | 1600 | 640 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 31; (11): Read/Write
| 41641 | 1640 | 668 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 32; (11): Read/Write
| 41681 | 1680 | 690 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 33; (11): Read/Write
| 41721 | 1720 | 6B8 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 34; (11): Read/Write
| 41761 | 1760 | 6E0 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 35; (11): Read/Write
| 41801 | 1800 | 708 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 36; (11): Read/Write
| 41841 | 1840 | 730 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 37; (11): Read/Write
| 41881 | 1880 | 758 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 38; (11): Read/Write
| 41921 | 1920 | 780 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 39; (11): Read/Write
| 41961 | 1960 | 7A8 | 3 | 16 | 40 | #REF! | (6): 80; (7): Configuration of node 40; (11): Read/Write
SETTING TIMEOUT VALUE OF DATA STATUS | 40354 | 353 | 161 | 3 | 16 | 1 | 194 | 2 | Cmp time 1 |  | 15 | uint16 | Read/Write | Time interval for Data status = 0
| 40355 | 354 | 162 | 3 | 16 | 1 | 196 | 2 | Cmp time 2 |  | 30 | uint16 | Read/Write | Time interval for Data status = 1
| 40356 | 355 | 163 | 3 | 16 | 1 | 198 | 2 | Cmp time 3 |  | 45 | uint16 | Read/Write | Time interval for Data status = 2
| 40357 | 356 | 164 | 3 | 16 | 1 | 200 | 2 | Cmp time 4 |  | 60 | uint16 | Read/Write | Time interval for Data status = 3
| 40358 | 357 | 165 | 3 | 16 | 1 | 202 | 2 | Cmp time 5 |  | 300 | uint16 | Read/Write | Time interval for Data status = 4
| 40359 | 358 | 166 | 3 | 16 | 1 | 204 | 2 | Cmp time 6 |  | 600 | uint16 | Read/Write | Time interval for Data status = 5
| 40360 | 359 | 167 | 3 | 16 | 1 | 206 | 2 | Cmp time 7 |  | 900 | uint16 | Read/Write | Time interval for Data status = 6
| 40361 | 360 | 168 | 3 | 16 | 1 | 208 | 2 | Cmp time 8 |  | 1800 | uint16 | Read/Write | Time interval for Data status = 7
| 40362 | 361 | 169 | 3 | 16 | 1 | 210 | 2 | Cmp time 9 |  | 3600 | uint16 | Read/Write | Time interval for Data status = 8
SETTING TIMEOUT VALUE OF RF TIMEOUT COUNT | 40363 | 362 | 16A | 16 |  | 1 | 212 | 2 | Timeout_count_threshold |  | 630 | uint16 | Read/Write | Time interval for Rf_timeout_count increase one more
RF MODE CONFIG | 40364 | 363 | 16B | 3 | 16 | 2 | 214 | 4 | Radio frequency | 433.05-434.79, 433 MHz | 433.92 | float | Read/Write | Only for advanced users. Configure the operating frequency of Co-ordinator, should be configured from 433.05-434.79 MHz.
| 40366 | 365 | 16D | 3 | 16 | 1 | 218 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Only for advanced users. Configure the RF power of Co-ordinator + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm
| 40367 | 366 | 16E | 3 | 16 | 1 | 220 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Only for advanced users. Configure the air data rate of Co-ordinator + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps
| 40368 | 367 | 16F | 3 | 16 | 1 | 218 | 2 | Rssi_threshold | -100…0 | -25 | int16 | Read/Write | RSSI value, this is the threshold to allow adding wireless sensors by RF when the rssi value is higher than the rssi_threshold. Should be configured from -14dBm to -40 dBm
| 40369 | 368 | 170 | 3 | 16 | 1 | 218 | 2 | Enb_auto_add_sensors | 0-1 | 0 | uint16 | Read/Write | "Enb_auto_add_sensors" = 1 when power on and this parameter will return to "0" after 5 minutes: + 1 => allow adding wireless sensors by RF + 0 => not allow adding wireless sensors by RF Write "Enb_auto_add_sensors" = 1 => this parameter will return to "0" after 5 minutes
TRAILER TRACKING CONFIG | 40370 | 369 | 171 | 3 | 16 | 26 | 214 | (6): 52; (7): Spare; (11): Read/Write
| 40396 | 395 | 18B | 3 | 16 | 1 | 266 | 2 | Trailer_rssi_threshold | (-100)-0 (dBm) | -60 | int16 | Read/Write | RSSI threshold value, this is the threshold minimum to detect a wireless active sensor tag when the rssi value is higher than the trailer_rssi_threshold
| 40397 | 396 | 18C | 3 | 16 | 1 | 268 | 2 | ASCII send_cycle | 1-3600s | 300 | uint16 | Read/Write | Every time interval of ASCII send_cycle(s), wireless tag receiver will absolutely send data to Black Box
| 40398 | 397 | 18D | 3 | 16 | 1 | 268 | 2 | ASCII enb | 0-1 | 1 | uint16 | Read/Write | 1: enable to send data to Black Box, 0: disable to send data to Black Box
DEVICE INFO | 40001 | 0 | 0 | 3 |  | 2 | 0 | 4 | Device info |  | WSCL | string | Read | Wireless sensor co-ordinator
| 40003 | 2 | 2 | 3 |  | 4 | 4 | 8 | Firmware version |  | 2 | string | Read
| 40007 | 6 | 6 | 3 |  | 2 | 12 | 4 | Hardware version |  | 2.4 | string | Read

## 26.LEC K1
MODBUS MEMORY MAP FOR WIRELESS DIGITAL CONDUCTIVITY SENSOR WS433-LEC-K1
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Ec value of sensor Node (parameter 1) | 0..2000 us/cm |  | float | Read | Value from digital conductivity sensor. This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) | 0oC..+50oC |  | float | Read | Value from digital conductivity sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 2 | 4 | Salinity |  |  | float | Read | ppm, Salinity value | for sensor with V5.x
| 30009 | 8 | 8 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30011 | 10 | A | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30013 | 12 | C | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30015 | 14 | E | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30017 | 16 | 10 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30019 | 18 | 12 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30021 | 20 | 14 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30023 | 22 | 16 | 4 |  | (5): 1; (6): 2; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | SENSOR_BOOT_TIME |  | 1 | uint16 | Read/Write | millisecond, if ws433-lec-k1 supply 15vdc for sensor => SENSOR_BOOT_TIME > 5000 ms | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40430 | 429 | 1AD | 3 | 16 | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40432 | 431 | 1AF | 3 | 16 | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40433 | 432 | 1B0 | 3 | 16 | (5): 5; (6): 10; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40438 | 437 | 1B5 | 3 | 16 | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 3 | 16 | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 3 | 16 | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 12.SMT07
MODBUS MEMORY MAP FOR WIRELESS SOIL MOISTURE SENSOR WS433-SMT-07
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Soil Moisture of sensor Node (parameter 1) | 0..100 (%) |  | float | Read | Value from soil moisture sensor. This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Soil Temperature of sensor Node (parameter 2) | -40oC..+80oC |  | float | Read | Value from soil moisture sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 2 | 4 | EC | 0..20000 us/cm |  | float | Read | us/cm, electrical conductivity value | for sensor with V5.x
| 30009 | 8 | 8 | 4 |  | 2 | 4 | Nitrogen | 1..1999 mg/kg |  | float | Read | mg/kg, nitrogen value | for sensor with V5.x
| 30011 | 10 | A | 4 |  | 2 | 4 | Phosphorus | 1..1999 mg/kg |  | float | Read | mg/kg, phosphorus value | for sensor with V5.x
| 30013 | 12 | C | 4 |  | 2 | 4 | Kali | 1..1999 mg/kg |  | float | Read | mg/kg, potassium value | for sensor with V5.x
| 30015 | 14 | E | 4 |  | 2 | 4 | Salinity | 0..10000 ppm |  | float | Read | ppm, Salinity value | for sensor with V5.x
| 30017 | 16 | 10 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30019 | 18 | 12 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30021 | 20 | 14 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30023 | 22 | 16 | 4 |  | (5): 1; (6): 2; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup |  | 900 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta |  | 3600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | SENSOR_BOOT_TIME |  | 2400 | uint32 | Read/Write | millisecond, the time for the sensor to reach a stable output | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40430 | 429 | 1AD | 3 | 16 | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40432 | 431 | 1AF | 3 | 16 | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40433 | 432 | 1B0 | 3 | 16 | (5): 5; (6): 10; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40438 | 437 | 1B5 | 3 | 16 | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 3 | 16 | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 3 | 16 | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 17.PH100
MODBUS MEMORY MAP FOR WIRELESS pH SENSOR WS433-PH100
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | pH value (prm 1) |  |  | float | Read | Value from pH sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value (prm 2) |  |  | float | Read | Value from pH sensor. This value is parameter 2 of a wireless sensor node
| 30007 | 6 | 6 | 4 |  | 2 | 4 | pH_ADC value |  |  | float | Read | Adc value of pH sensor
| 30009 | 8 | 8 | 4 |  | 2 | 4 | pH_mV value |  |  | float | Read | mV value of pH sensor
| 30011 | 10 | A | 4 |  | 2 | 4 | PT100_Res value |  |  | float | Read | Resistance value of pt100 sensor
30001
30001
30001
30001
30001
30001
30001
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup |  | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta |  | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 3 | 6 | spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40422 | 421 | 1A5 | 3 | 16 | 2 | 4 | wire resistance |  | 1.74 | float | Read/Write | Ohm, Compensate for conductor resistance | for sensor with V5.x
| 40424 | 423 | 1A7 | 3 | 16 | 2 | 4 | Manual_Temp_Input |  | 0 | float | Read/Write | Temperature value. When there is no temperature sensor, turn on Manual_Temp_Enb = 1 then Temperature (prm 2) = Manual_Temp_Input | for sensor with V5.x
| 40426 | 425 | 1A9 | 3 | 16 | 1 | 2 | Manual_Temp_Enb |  | 0 | uint16 | Read/Write | When there is no temperature sensor, turn on Manual_Temp_Enb = 1, then Temperature (prm 2) = Manual_Temp_Input | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | SENSOR_BOOT_TIME |  | 100 | uint16 | Read/Write | millisecond, the time for the sensor to reach a stable output | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | calibEnb |  | 0 | uint16 | Read/Write | Before calibration, must turn on caribE = 1. After calibration, set calibEnb = 0 | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 2 | 4 | pHFeedback |  |  | float | Read/Write | Step 1: Calibrate with standard solution pH = 7.01, wait for about 3 minutes for the reading to stabilize, write 7 down to pHFeedback Step 2: Calibrate with standard solution pH = 4.01 or 10.01, wait about 3 minutes for reading to stabilize, write down pHFeedback pH value of solution | for sensor with V5.x
| 40431 | 430 | 1AE | 3 | 16 | 2 | 4 | pHFactor |  |  | float | Read |  | for sensor with V5.x
| 40433 | 432 | 1B0 | 3 | 16 | 2 | 4 | pH7_adc |  |  | float | Read |  | for sensor with V5.x
| 40435 | 434 | 1B2 | 3 | 16 | 2 | 4 | pH7_mV |  |  | float | Read |  | for sensor with V5.x
| 40437 | 436 | 1B4 | 3 | 16 | 1 | 2 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 3 | 16 | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 3 | 16 | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 3 | 16 | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 19.PPCT
MODBUS MEMORY MAP FOR WIRELESS PEOPLE COUNTER SENSOR WS433-PPCT
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 1 | 2 | NRC_People_In |  |  | uint16 | Read | Non-resettable counter
| 30003 | 2 | 2 | 4 |  | 1 | 2 | NRC_People_Out |  |  | uint16 | Read | Non-resettable counter
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 1 | 2 | RC_People_In |  |  | uint16 | Read | Reset to 0 after sending to Coordinator
| 30006 | 5 | 5 | 4 |  | 1 | 2 | RC_People_Out |  |  | uint16 | Read | Reset to 0 after sending to Coordinator
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Dist_front_zone |  |  | int16 | Read | Distance of front zone
| 30008 | 7 | 7 | 4 |  | 1 | 2 | Dist_back_zone |  |  | int16 | Read | Distance of back zone
30001
30001
30001
30001
30001
30001
30001
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup |  | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta |  | 3600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Not Applicable. Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | Count_threshold |  | 20 | uint16 | Read/Write | Threshold count on how many people send Coordinator | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | Dist_threshold |  | 1600 | uint16 | Read/Write | Threshold setting for laser sensor to distinguish between when people are present and when no one is standing under the sensor The laser sensor will measure the distance value from the sensor (ceiling) to the floor. + When there are people, the measured laser sensor value < Dist_threshold + When there is no person, the measured laser sensor value > Dist_threshold | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 1 | 2 | Dist_hys |  | 100 | uint16 | Read/Write | Hysteresis of Dist_threshold | for sensor with V5.x
| 40430 | 429 | 1AD | 3 | 16 | 1 | 2 | Inter_meas_period |  | 48 | uint16 | Read/Write | The sampling time of the sensor laser | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 5 | 10 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40436 | 435 | 1B3 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40437 | 436 | 1B4 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 18.NH3
MODBUS MEMORY MAP FOR WIRELESS AMMONIA SENSOR WS433-NH3
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Ammonia value of sensor Node (parameter 1) | ppm |  | float | Read | Value from ammonia sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) | oC |  | float | Read | Value from ammonia sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | System_sensitivity |  | 11 | float | Read/Write | The sensitivity of the circuit (mV/ppm) | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 7 | 14 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-TCT (hidden)
MODBUS MEMORY MAP FOR WIRELESS TYPE T THERMOCOUPLE SENSOR WS433-TCT
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Temperature value of Thermocouple (parameter 1) | -250oC..+400oC |  | float | Read | Value from type T thermocouple sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of cold-junction compensation (parameter 2) | -20oC..+85oC |  | float | Read | Value from type T thermocouple sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 12.SMT01
MODBUS MEMORY MAP FOR WIRELESS SOIL MOISTURE SENSOR WS433-SMT-01
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Soil Moisture of sensor Node (parameter 1) | 0..100 (%) |  | float | Read | Value from soil moisture sensor. This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Soil Temperature of sensor Node (parameter 2) | -30oC..+70oC |  | float | Read | Value from soil moisture sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40429 | 428 | 1AC | 16 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | (5): 5; (6): 10; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 24.CO2
MODBUS MEMORY MAP FOR WIRELESS CO2 SENSOR WITH HUMIDITY & TEMPERATURE
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | CO2 value of sensor Node | 400..40000 ppm |  | float | Read | Value from Wireless CO2 sensor | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Humidity value of sensor Node | 0..100%RH |  | float | Read | Value from Wireless CO2 sensor | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 2 | 4 | Temperature value of sensor Node | -40..+70oC |  | float | Read | Value from Wireless CO2 sensor | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value of The RMS Acceleration value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | CO2_calc_time |  | 6 | uint16 | Read/Write | Second, response time of sensor | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | 10 | 20 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with >= V5.x
| 40438 | 437 | 1B5 | 3 | 16 | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with >= V5.x
| 40439 | 438 | 1B6 | 3 | 16 | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 3 | 16 | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with version >= V6.x

## 16.V1A
MODBUS MEMORY MAP FOR WIRELESS 1-AXIS VIBRATION SENSOR WS433-V1A
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Frequency value of sensor Node | Hz |  | float | Read | Value from V1A sensor | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Peak Acceleration value of sensor Node | m / s2 |  | float | Read | Value from V1A sensor | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 2 | 4 | RMS Acceleration value of sensor Node | m / s2 |  | float | Read | Value from V1A sensor | for sensor with V5.x
| 30009 | 8 | 8 | 4 |  | 2 | 4 | Peak Velocity value of sensor Node | mm / s |  | float | Read | Value from V1A sensor | for sensor with V5.x
| 30011 | 10 | A | 4 |  | 2 | 4 | RMS Velocity value of sensor Node | mm / s |  | float | Read | Value from V1A sensor | for sensor with V5.x
| 30013 | 12 | C | 4 |  | 2 | 4 | PeakPeak Distance value of sensor Node | um |  | float | Read | Value from V1A sensor | for sensor with V5.x
| 30015 | 14 | E | 4 |  | 2 | 4 | RMS Distance value of sensor Node | um |  | float | Read | Value from V1A sensor | for sensor with V5.x
| 30017 | 16 | 10 | 4 |  | 2 | 4 | Temperature value of sensor Node | -40..+125oC |  | float | Read | Value from V1A sensor | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | (5): 1; (6): 2; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with >= V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with >= V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with version >= V6.x

## 14.ULA & ULB & ULC
MODBUS MEMORY MAP FOR WIRELESS ULTRASONIC LEVEL SENSOR WS433-ULB & ULC
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Level value of sensor Node (parameter 1) | mm |  | float | Read | Value from ultrasonic level sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Distance value of sensor Node (parameter 2) | mm |  | float | Read | Value from ultrasonic level sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 1.ATE
MODBUS MEMORY MAP FOR WIRELESS TEMPERATURE SENSOR WS433-M12F WITH ATE-xx
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 1) | -40..+125oC |  | float | Read | Value from temperature sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | Same value as parameter 1 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 21.PT100
MODBUS MEMORY MAP FOR WIRELESS RTD PT100 SENSOR WS433-M12F WITH PT100
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | PT100 Temperature value of sensor Node (parameter 1) | -200..750oC |  | float | Read | Value from RTD PT100 sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | PT100 Resistance value of sensor Node (parameter 2) | 18..360 ohm |  | float | Read | Value from RTD PT100 sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 2.ATH
MODBUS MEMORY MAP FOR WIRELESS HUMIDITY SENSOR WS433-M12F WITH ATH
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Humidity value of sensor Node (parameter 1) | 0..100% |  | float | Read | Value from humidity sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from humidity sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 3.ADP
MODBUS MEMORY MAP FOR WIRELESS DIFFERENTIAL PRESSURE SENSOR WS433-M12F WITH ADP
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Differential Pressure value of sensor Node (parameter 1) | -125..+125Pa |  | float | Read | Value from differential pressure sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from differential pressure sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 4.PPS
MODBUS MEMORY MAP FOR WIRELESS PRESSURE SENSOR WS433-M12F WITH PPS
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Pressure value of sensor Node (parameter 1) | 0..100% |  | float | Read | Value from pressure process sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from pressure process sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 8.ALS
MODBUS MEMORY MAP FOR WIRELESS DIFFERENTIAL PRESSURE SENSOR WS433-M12F WITH AMBIENT LIGHT SENSOR
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | illuminance value of sensor Node (parameter 1) | 20.48..+83865.6 |  | float | Read | Value from ambient light sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | Same value as parameter 1 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 5.AC
MODBUS MEMORY MAP FOR WIRELESS AC CURRENT SENSOR WS433-AC
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | AC Current value of sensor Node (parameter 1) | A |  | float | Read | Value from ac current sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | Same value as parameter 1 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | CT_factor |  | 40 | float | Read/Write | CT factor value of Current Transformer | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 2 | 4 | Cutoff_current |  | 0.5 | float | Read/Write | Cut-off current value, this is the threshold to force ac current value = 0 when the load current is less then the threshold | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 7 | 14 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 7.DI and Status
MODBUS MEMORY MAP FOR WIRELESS DIGITAL INPUT SENSOR WS433-DI WITH 2 STATUS INPUT
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 1 | 2 | Digital status 1 of sensor Node (parameter 1) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value is parameter 1 of a wireless sensor node
| 30003 | 2 | 2 | 4 |  | 1 | 2 | Digital status 2 of sensor Node (parameter 2) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value is parameter 2 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 1 | 2 | Digital toggle 1 of sensor Node (parameter 1) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value will toggle when detecting rising-edge
| 30006 | 5 | 5 | 4 |  | 1 | 2 | Digital toggle 2 of sensor Node (parameter 2) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value will toggle when detecting rising-edge | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | (5): 1; (6): 2; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 1 | 2 | Filter time 1 | 1-65535 | 100 | uint16 | Read/Write | Pulse width value = Filter time x 3: for the digital input 1, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 1 | 2 | Filter time 2 | 1-65535 | 100 | uint16 | Read/Write | Pulse width value = Filter time x 3: for the digital input 2, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | 5 | 10 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 6.DI and Counter
MODBUS MEMORY MAP FOR WIRELESS DIGITAL INPUT SENSOR WS433-DI WITH 2 COUNTER INPUT
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Counter value 1 of sensor Node (parameter 1) | 0-999,999,999 |  | uint32 | Read | Value from digital input sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Counter value 2 of sensor Node (parameter 2) | 0-999,999,999 |  | uint32 | Read | Value from digital input sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | (5): 1; (6): 2; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30012 | 11 | B | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30014 | 13 | D | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30016 | 15 | F | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | Counter value 1 | 0-999,999,999 |  | uint32 | Read/Write | This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 2 | 4 | Counter value 2 | 0-999,999,999 |  | uint32 | Read/Write | This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 1 | 2 | Filter time 1 | 1-65535 | 100 | uint16 | Read/Write | Pulse width value for the digital input 1, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 1 | 2 | Filter time 2 | 1-65535 | 100 | uint16 | Read/Write | Pulse width value for the digital input 2, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | 5 | 10 | Spare | 5-65535 |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock | 1-65535 | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 | 1-65535 | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 | 1-65535 | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 10.RL
MODBUS MEMORY MAP FOR WIRELESS RELAY OUTPUT SENSOR WS433-RL
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
Control Data * This control data will sent to sensor node immediately | 42001 | 2000 | 7D0 | 3 | 16 | 1 | 2 | Control Relay 1 of sensor Node | 0-1 | 0 | uint16 | Read/Write | 0: turn off relay 1 1: turn on relay 1
| 42002 | 2001 | 7D1 | 3 | 16 | 1 | 2 | Control Relay 2 of sensor Node | 0-1 | 0 | uint16 | Read/Write | 0: turn off relay 2 1: turn on relay 2
| 42003 | 2002 | 7D2 | 3 | 16 | 1 | 2 | Control Relay 3 of sensor Node | 0-1 | 0 | uint16 | Read/Write | 0: turn off relay 3 1: turn on relay 3
| 42004 | 2003 | 7D3 | 3 | 16 | 1 | 2 | Control Relay 4 of sensor Node | 0-1 | 0 | uint16 | Read/Write | 0: turn off relay 4 1: turn on relay 4
| 42005 | 2004 | 7D4 | 3 | 16 | (5): 4; (6): 8
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | (5): 1; (6): 2
| 30002 | 1 | 1 | 4 |  | 1 | 2 | Status Relay 1 of sensor Node |  |  | uint16 | Read | Value from relay output sensor, this value is status of relay 1 for a wireless sensor node
| 30003 | 2 | 2 | 4 |  | 1 | 2 | Status Relay 2 of sensor Node |  |  | uint16 | Read | Value from relay output sensor, this value is status of relay 2 for a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 1 | 2 | Status Relay 3 of sensor Node |  |  | uint16 | Read | Value from relay output sensor, this value is status of relay 3 for a wireless sensor node
| 30006 | 5 | 5 | 4 |  | 1 | 2 | Status Relay 4 of sensor Node |  |  | uint16 | Read | Value from relay output sensor, this value is status of relay 4 for a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | (5): 1; (6): 2; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40411 | 410 | 19A | 3 |  | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | (5): 2; (6): 4; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | Default relay 1 | 0-2 | 0 | uint16 | Read/Write | 0: off, 1: on, 2: last state (Restores the previous power state before power loss occurs) | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | Default relay 2 | 0-2 | 0 | uint16 | Read/Write | 0: off, 1: on, 2: last state (Restores the previous power state before power loss occurs) | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 1 | 2 | Default relay 3 | 0-2 | 0 | uint16 | Read/Write | 0: off, 1: on, 2: last state (Restores the previous power state before power loss occurs) | for sensor with V5.x
| 40430 | 429 | 1AD | 3 | 16 | 1 | 2 | Default relay 4 | 0-2 | 0 | uint16 | Read/Write | 0: off, 1: on, 2: last state (Restores the previous power state before power loss occurs) | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 7 | 14 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 9.Oxy
MODBUS MEMORY MAP FOR WIRELESS OXY SENSOR WS433-O2
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Oxy value of sensor Node (parameter 1) | % |  | float | Read | Value from Oxy sensor. This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from Oxy sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | Response_time | ms | 0 | uint16 | Read/Write | Actual times for Field Instruments to output data. This value will vary dependent on Field Instruments | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | Response_time_max | 100-65535 ms | 3000 | uint16 | Read/Write | This is the maximum preset value for response time | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 1 | 2 | Run_mode | 0-1 | 0 | uint16 | Read/Write | "Run_mode" = 1 when power on and this parameter will return to "0" after 5 cycles send data to co-ordinator: + 1 => allow auto-detect response time after some cycle send data to co-ordinator + 0 => stop auto-detect response time Write "Run_mode" = 1 => this parameter will return to "0" after 5 cycles send data to co-ordinator | for sensor with V5.x
| 40430 | 429 | 1AD | 3 | 16 | 2 | 4 | Cutoff |  | 0 | float | Read/Write | Cut-off value, this is the threshold to force Analog value 1 of sensor Node = 0 when it is less then the threshold | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 6 | 12 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 9.AI
MODBUS MEMORY MAP FOR WIRELESS ANALOG INPUT SENSOR WS433-AI
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Analog value 1 of sensor Node (parameter 1) |  |  | float | Read | Value from Analog input sensor. This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | Same value as parameter 1 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | Response_time | ms | 0 | uint16 | Read/Write | Actual times for Field Instruments to output data. This value will vary dependent on Field Instruments | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | Response_time_max | 100-65535 ms | 3000 | uint16 | Read/Write | This is the maximum preset value for response time | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 1 | 2 | Run_mode | 0-1 | 0 | uint16 | Read/Write | "Run_mode" = 1 when power on and this parameter will return to "0" after 5 cycles send data to co-ordinator: + 1 => allow auto-detect response time after some cycle send data to co-ordinator + 0 => stop auto-detect response time Write "Run_mode" = 1 => this parameter will return to "0" after 5 cycles send data to co-ordinator | for sensor with V5.x
| 40430 | 429 | 1AD | 3 | 16 | 2 | 4 | Cutoff |  | 0 | float | Read/Write | Cut-off value, this is the threshold to force Analog value 1 of sensor Node = 0 when it is less then the threshold | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 6 | 12 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-CAPSM v6.0 (hidden)
MODBUS MEMORY MAP FOR WIRELESS SOIL MOISTURE SENSOR WS433-CAPSM-02
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Soil moisture of sensor Node (parameter 1) | 0-100 (%) |  | float | Read | Value from soil moisture sensor. This value is parameter 1 of a wireless sensor node | for sensor with V6.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node | -30oC…+70oC |  | float | Read | Value from soil moisture sensor. This value is parameter 2 of a wireless sensor node | for sensor with V6.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V6.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V6.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V6.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V6.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V6.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V6.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V6.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V6.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V6.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V6.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V6.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V6.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V6.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V6.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V6.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V6.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V6.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V6.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V6.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V6.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V6.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V6.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V6.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V6.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V6.x
| 40427 | 426 | 1AA | 16 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40429 | 428 | 1AC | 16 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | (5): 5; (6): 10; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## 11.CAPSM v7.0
MODBUS MEMORY MAP FOR WIRELESS SOIL MOISTURE - E.C - TEMPERATURE SENSOR WS433-CAPSM-02
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Soil moisture of sensor Node (parameter 1) | 0-1000 (‰) |  | float | Read | Soil moisture value. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node | -30oC…+70oC |  | float | Read | Soil temperature sensor
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold.
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2
| 40427 | 426 | 1AA | 16 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40429 | 428 | 1AC | 16 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | (5): 5; (6): 10; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-GYRO v6.0 (hidden)
MODBUS MEMORY MAP FOR WIRELESS GYRO & ACCELEROMETE SENSOR
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Tilt axis X (prm1) | -90⁰..+90⁰ |  | float | Read | Value from gyro & acceleromete sensor. This value is parameter 1 of a wireless sensor node | for sensor with V6.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type | for sensor with V6.x
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Tilt axis Y (prm2) | -90⁰..+90⁰ |  | float | Read | Value from gyro & acceleromete sensor. This value is parameter 2 of a wireless sensor node | for sensor with V6.x
| 30007 | 6 | 6 | 4 |  | 2 | 4 | Tilt axis Z (prm3) | -90⁰..+90⁰ |  | float | Read | Value from gyro & acceleromete sensor. This value is parameter 3 of a wireless sensor node | for sensor with V6.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V6.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V6.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V6.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V6.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V6.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V6.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V6.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V6.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V6.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V6.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V6.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_axisX |  | 0 | float | Read/Write | Delta value for Tilt axis X, this is the threshold to allow sending data to co-ordinator when the new value of Tilt axis X is changed from the last value a delta value which is higher than the threshold. | for sensor with V6.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V6.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V6.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V6.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V6.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | Delta_axisY |  | 0 | float | Read/Write | Delta value for Tilt axis Y, this is the threshold to allow sending data to co-ordinator when the new value of Tilt axis Y is changed from the last value a delta value which is higher than the threshold. | for sensor with V6.x
| 40429 | 428 | 1AC | 3 | 16 | 2 | 4 | Delta_axisZ |  | 0 | float | Read/Write | Delta value for Tilt axis Z, this is the threshold to allow sending data to co-ordinator when the new value of Tilt axis Z is changed from the last value a delta value which is higher than the threshold. | for sensor with V6.x
| 40431 | 430 | 1AE | 16 |  | 1 | 2 | Pulse width 1 |  | 90 | uint16 | Read/Write | Pulse width value for the digital input 1, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 1 | 2 | Pulse width 2 |  | 90 | uint16 | Read/Write | Pulse width value for the digital input 2, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | 5 | 10 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of 1-wire (hidden)
MODBUS MEMORY MAP FOR WIRELESS TEMPERATURE SENSOR WS433-M12F WITH ATE-xx
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (10): float; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 1 | 2 | TempC 1 |  |  | int16 | Read | Temperature of 1-wire-sensor 1 | for sensor with V5.x
| 30006 | 5 | 5 | 4 |  | 1 | 2 | TempC 2 |  |  | int16 | Read | Temperature of 1-wire-sensor 2 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | TempC 3 |  |  | int16 | Read | Temperature of 1-wire-sensor 3 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 1 | 2 | TempC 4 |  |  | int16 | Read | Temperature of 1-wire-sensor 4 | for sensor with V5.x
| 30009 | 8 | 8 | 4 |  | 1 | 2 | TempC 5 |  |  | int16 | Read | Temperature of 1-wire-sensor 5 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 1 | 2 | TempC 6 |  |  | int16 | Read | Temperature of 1-wire-sensor 6 | for sensor with V5.x
| 30011 | 10 | A | 4 |  | 1 | 2 | TempC 7 |  |  | int16 | Read | Temperature of 1-wire-sensor 7 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 1 | 2 | TempC 8 |  |  | int16 | Read | Temperature of 1-wire-sensor 8 | for sensor with V5.x
| 30013 | 12 | C | 4 |  | 1 | 2 | TempC 9 |  |  | int16 | Read | Temperature of 1-wire-sensor 9 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 1 | 2 | TempC 10 |  |  | int16 | Read | Temperature of 1-wire-sensor 10
| 30015 | 14 | E | 4 |  | 1 | 2 | TempC 11 |  |  | int16 | Read | Temperature of 1-wire-sensor 11
| 30016 | 15 | F | 4 |  | 1 | 2 | TempC 12 |  |  | int16 | Read | Temperature of 1-wire-sensor 12
| 30017 | 16 | 10 | 4 |  | 1 | 2 | TempC 13 |  |  | int16 | Read | Temperature of 1-wire-sensor 13
| 30018 | 17 | 11 | 4 |  | 1 | 2 | TempC 14 |  |  | int16 | Read | Temperature of 1-wire-sensor 14
| 30019 | 18 | 12 | 4 |  | 1 | 2 | TempC 15 |  |  | int16 | Read | Temperature of 1-wire-sensor 15
| 30020 | 19 | 13 | 4 |  | 1 | 2 | TempC 16 |  |  | int16 | Read | Temperature of 1-wire-sensor 16
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 1 | 2 | 1wire id 1 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40420 | 419 | 1A3 | 3 | 16 | 1 | 2 | 1wire id 2 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40421 | 420 | 1A4 | 3 | 16 | 1 | 2 | 1wire id 3 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40422 | 421 | 1A5 | 3 | 16 | 1 | 2 | 1wire id 4 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40423 | 422 | 1A6 | 3 | 16 | 1 | 2 | 1wire id 5 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40424 | 423 | 1A7 | 3 | 16 | 1 | 2 | 1wire id 6 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40425 | 424 | 1A8 | 3 | 16 | 1 | 2 | 1wire id 7 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40426 | 425 | 1A9 | 3 | 16 | 1 | 2 | 1wire id 8 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | 1wire id 9 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | 1wire id 10 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40429 | 428 | 1AC | 3 | 16 | 1 | 2 | 1wire id 11 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40430 | 429 | 1AD | 3 | 16 | 1 | 2 | 1wire id 12 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40431 | 430 | 1AE | 3 | 16 | 1 | 2 | 1wire id 13 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40432 | 431 | 1AF | 3 | 16 | 1 | 2 | 1wire id 14 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40433 | 432 | 1B0 | 3 | 16 | 1 | 2 | 1wire id 15 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40434 | 433 | 1B1 | 3 | 16 | 1 | 2 | 1wire id 16 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40435 | 434 | 1B2 | 3 | 16 | 1 | 2 | run mode |  |  | unit16 | Read/Write | 0: add 1wire, 1: read tempC
| 40436 | 435 | 1B3 | 3 | 16 | 1 | 2 | read retry times |  | 0 | unit16 | Read/Write
| 40001 | 0 | 0 | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40012 | 11 | B | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40013 | 12 | C | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40014 | 13 | D | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x