## Memmap of WS433-CL V1.9
MODBUS MEMORY MAP of WS433-CL Version 1.9
For Simple operation, just set up the "ADDING WIRELESS SENSORS"
| (1) | (2) | (3) | (4) |  | (5) |  | (6) | (7) | (8) | (9) | (10) | (11) | (12)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of Register | Adr | Byte Size | Description | Range | Default | Format | Property | Comment
ADDING WIRELESS SENSORS | 40273 | 272 | 110 | 3 | 16 | 1 | 32 | 2 | Num of Node |  | 0 | uint16 | Read/Write | Write "num of node" = 0 => allow deleting to all node-id of co-ordinator
| 40274 | 273 | 111 | 3 | 16 | 2 | 34 | 4 | Node id 1 |  | 0 | uint32 | Read/Write | Config the ID number of each wireless sensor (the last 9 digits of sensor's S/N)
| 40276 | 275 | 113 | 3 | 16 | 2 | 38 | 4 | Node id 2 |  | 0 | uint32 | Read/Write
| 40278 | 277 | 115 | 3 | 16 | 2 | 42 | 4 | Node id 3 |  | 0 | uint32 | Read/Write
| 40280 | 279 | 117 | 3 | 16 | 2 | 46 | 4 | Node id 4 |  | 0 | uint32 | Read/Write
| 40282 | 281 | 119 | 3 | 16 | 2 | 50 | 4 | Node id 5 |  | 0 | uint32 | Read/Write
| 40284 | 283 | 11B | 3 | 16 | 2 | 54 | 4 | Node id 6 |  | 0 | uint32 | Read/Write
| 40286 | 285 | 11D | 3 | 16 | 2 | 58 | 4 | Node id 7 |  | 0 | uint32 | Read/Write
| 40288 | 287 | 11F | 3 | 16 | 2 | 62 | 4 | Node id 8 |  | 0 | uint32 | Read/Write
| 40290 | 289 | 121 | 3 | 16 | 2 | 66 | 4 | Node id 9 |  | 0 | uint32 | Read/Write
| 40292 | 291 | 123 | 3 | 16 | 2 | 70 | 4 | Node id 10 |  | 0 | uint32 | Read/Write
| 40294 | 293 | 125 | 3 | 16 | 2 | 74 | 4 | Node id 11 |  | 0 | uint32 | Read/Write
| 40296 | 295 | 127 | 3 | 16 | 2 | 78 | 4 | Node id 12 |  | 0 | uint32 | Read/Write
| 40298 | 297 | 129 | 3 | 16 | 2 | 82 | 4 | Node id 13 |  | 0 | uint32 | Read/Write
| 40300 | 299 | 12B | 3 | 16 | 2 | 86 | 4 | Node id 14 |  | 0 | uint32 | Read/Write
| 40302 | 301 | 12D | 3 | 16 | 2 | 90 | 4 | Node id 15 |  | 0 | uint32 | Read/Write
| 40304 | 303 | 12F | 3 | 16 | 2 | 94 | 4 | Node id 16 |  | 0 | uint32 | Read/Write
| 40306 | 305 | 131 | 3 | 16 | 2 | 98 | 4 | Node id 17 |  | 0 | uint32 | Read/Write
| 40308 | 307 | 133 | 3 | 16 | 2 | 102 | 4 | Node id 18 |  | 0 | uint32 | Read/Write
| 40310 | 309 | 135 | 3 | 16 | 2 | 106 | 4 | Node id 19 |  | 0 | uint32 | Read/Write
| 40312 | 311 | 137 | 3 | 16 | 2 | 110 | 4 | Node id 20 |  | 0 | uint32 | Read/Write
| 40314 | 313 | 139 | 3 | 16 | 2 | 114 | 4 | Node id 21 |  | 0 | uint32 | Read/Write
| 40316 | 315 | 13B | 3 | 16 | 2 | 118 | 4 | Node id 22 |  | 0 | uint32 | Read/Write
| 40318 | 317 | 13D | 3 | 16 | 2 | 122 | 4 | Node id 23 |  | 0 | uint32 | Read/Write
| 40320 | 319 | 13F | 3 | 16 | 2 | 126 | 4 | Node id 24 |  | 0 | uint32 | Read/Write
| 40322 | 321 | 141 | 3 | 16 | 2 | 130 | 4 | Node id 25 |  | 0 | uint32 | Read/Write
| 40324 | 323 | 143 | 3 | 16 | 2 | 134 | 4 | Node id 26 |  | 0 | uint32 | Read/Write
| 40326 | 325 | 145 | 3 | 16 | 2 | 138 | 4 | Node id 27 |  | 0 | uint32 | Read/Write
| 40328 | 327 | 147 | 3 | 16 | 2 | 142 | 4 | Node id 28 |  | 0 | uint32 | Read/Write
| 40330 | 329 | 149 | 3 | 16 | 2 | 146 | 4 | Node id 29 |  | 0 | uint32 | Read/Write
| 40332 | 331 | 14B | 3 | 16 | 2 | 150 | 4 | Node id 30 |  | 0 | uint32 | Read/Write
| 40334 | 333 | 14D | 3 | 16 | 2 | 154 | 4 | Node id 31 |  | 0 | uint32 | Read/Write
| 40336 | 335 | 14F | 3 | 16 | 2 | 158 | 4 | Node id 32 |  | 0 | uint32 | Read/Write
| 40338 | 337 | 151 | 3 | 16 | 2 | 162 | 4 | Node id 33 |  | 0 | uint32 | Read/Write
| 40340 | 339 | 153 | 3 | 16 | 2 | 166 | 4 | Node id 34 |  | 0 | uint32 | Read/Write
| 40342 | 341 | 155 | 3 | 16 | 2 | 170 | 4 | Node id 35 |  | 0 | uint32 | Read/Write
| 40344 | 343 | 157 | 3 | 16 | 2 | 174 | 4 | Node id 36 |  | 0 | uint32 | Read/Write
| 40346 | 345 | 159 | 3 | 16 | 2 | 178 | 4 | Node id 37 |  | 0 | uint32 | Read/Write
| 40348 | 347 | 15B | 3 | 16 | 2 | 182 | 4 | Node id 38 |  | 0 | uint32 | Read/Write
| 40350 | 349 | 15D | 3 | 16 | 2 | 186 | 4 | Node id 39 |  | 0 | uint32 | Read/Write
| 40352 | 351 | 15F | 3 | 16 | 2 | 190 | 4 | Node id 40 |  | 0 | uint32 | Read/Write
MODBUS PORT CONFIG | 40257 | 256 | 100 | 3 | 16 | 1 | 0 | 2 | Modbus address | 1-247 | 1 | uint16 | Read/Write
| 40258 | 257 | 101 | 3 | 16 | 1 | 2 | 2 | Modbus baudrate | 0-1 | 0 | uint16 | Read/Write | 0: 9600, 1: 19200
| 40259 | 258 | 102 | 3 | 16 | 1 | 4 | 2 | Modbus parity | 0-2 | 0 | uint16 | Read/Write | 0: none, 1: odd, 2: even
OPERATION DATA OF 40 WIRELESS SENSORS | 30001 | 0 | 0 | 4 |  | 32 |  | 64 | Data area of Node 1 |  |  |  | Read | Details in sheet of sensor
| 30033 | 32 | 20 | 4 |  | 32 |  | 64 | Data area of Node 2 |  |  |  | Read
| 30065 | 64 | 40 | 4 |  | 32 |  | 64 | Data area of Node 3 |  |  |  | Read
| 30097 | 96 | 60 | 4 |  | 32 |  | 64 | Data area of Node 4 |  |  |  | Read
| 30129 | 128 | 80 | 4 |  | 32 |  | 64 | Data area of Node 5 |  |  |  | Read
| 30161 | 160 | A0 | 4 |  | 32 |  | 64 | Data area of Node 6 |  |  |  | Read
| 30193 | 192 | C0 | 4 |  | 32 |  | 64 | Data area of Node 7 |  |  |  | Read
| 30225 | 224 | E0 | 4 |  | 32 |  | 64 | Data area of Node 8 |  |  |  | Read
| 30257 | 256 | 100 | 4 |  | 32 |  | 64 | Data area of Node 9 |  |  |  | Read
| 30289 | 288 | 120 | 4 |  | 32 |  | 64 | Data area of Node 10 |  |  |  | Read
| 30321 | 320 | 140 | 4 |  | 32 |  | 64 | Data area of Node 11 |  |  |  | Read
| 30353 | 352 | 160 | 4 |  | 32 |  | 64 | Data area of Node 12 |  |  |  | Read
| 30385 | 384 | 180 | 4 |  | 32 |  | 64 | Data area of Node 13 |  |  |  | Read
| 30417 | 416 | 1A0 | 4 |  | 32 |  | 64 | Data area of Node 14 |  |  |  | Read
| 30449 | 448 | 1C0 | 4 |  | 32 |  | 64 | Data area of Node 15 |  |  |  | Read
| 30481 | 480 | 1E0 | 4 |  | 32 |  | 64 | Data area of Node 16 |  |  |  | Read
| 30513 | 512 | 200 | 4 |  | 32 |  | 64 | Data area of Node 17 |  |  |  | Read
| 30545 | 544 | 220 | 4 |  | 32 |  | 64 | Data area of Node 18 |  |  |  | Read
| 30577 | 576 | 240 | 4 |  | 32 |  | 64 | Data area of Node 19 |  |  |  | Read
| 30609 | 608 | 260 | 4 |  | 32 |  | 64 | Data area of Node 20 |  |  |  | Read
| 30641 | 640 | 280 | 4 |  | 32 |  | 64 | Data area of Node 21 |  |  |  | Read
| 30673 | 672 | 2A0 | 4 |  | 32 |  | 64 | Data area of Node 22 |  |  |  | Read
| 30705 | 704 | 2C0 | 4 |  | 32 |  | 64 | Data area of Node 23 |  |  |  | Read
| 30737 | 736 | 2E0 | 4 |  | 32 |  | 64 | Data area of Node 24 |  |  |  | Read
| 30769 | 768 | 300 | 4 |  | 32 |  | 64 | Data area of Node 25 |  |  |  | Read
| 30801 | 800 | 320 | 4 |  | 32 |  | 64 | Data area of Node 26 |  |  |  | Read
| 30833 | 832 | 340 | 4 |  | 32 |  | 64 | Data area of Node 27 |  |  |  | Read
| 30865 | 864 | 360 | 4 |  | 32 |  | 64 | Data area of Node 28 |  |  |  | Read
| 30897 | 896 | 380 | 4 |  | 32 |  | 64 | Data area of Node 29 |  |  |  | Read
| 30929 | 928 | 3A0 | 4 |  | 32 |  | 64 | Data area of Node 30 |  |  |  | Read
| 30961 | 960 | 3C0 | 4 |  | 32 |  | 64 | Data area of Node 31 |  |  |  | Read
| 30993 | 992 | 3E0 | 4 |  | 32 |  | 64 | Data area of Node 32 |  |  |  | Read
| 31025 | 1024 | 400 | 4 |  | 32 |  | 64 | Data area of Node 33 |  |  |  | Read
| 31057 | 1056 | 420 | 4 |  | 32 |  | 64 | Data area of Node 34 |  |  |  | Read
| 31089 | 1088 | 440 | 4 |  | 32 |  | 64 | Data area of Node 35 |  |  |  | Read
| 31121 | 1120 | 460 | 4 |  | 32 |  | 64 | Data area of Node 36 |  |  |  | Read
| 31153 | 1152 | 480 | 4 |  | 32 |  | 64 | Data area of Node 37 |  |  |  | Read
| 31185 | 1184 | 4A0 | 4 |  | 32 |  | 64 | Data area of Node 38 |  |  |  | Read
| 31217 | 1216 | 4C0 | 4 |  | 32 |  | 64 | Data area of Node 39 |  |  |  | Read
| 31249 | 1248 | 4E0 | 4 |  | 32 |  | 64 | Data area of Node 40 |  |  |  | Read
OPERATION DATA OF 40 WIRELESS SENSORS FOR ICONNECTOR (*) | 81217 | 41216 | A100 | 3 |  | 256 |  | 512 | Data area of Node 1 |  |  |  | Read | Details in sheet of sensor
| 81473 | 41472 | A200 | 3 |  | 256 |  | 512 | Data area of Node 2 |  |  |  | Read
| 81729 | 41728 | A300 | 3 |  | 256 |  | 512 | Data area of Node 3 |  |  |  | Read
| 81985 | 41984 | A400 | 3 |  | 256 |  | 512 | Data area of Node 4 |  |  |  | Read
| 82241 | 42240 | A500 | 3 |  | 256 |  | 512 | Data area of Node 5 |  |  |  | Read
| 82497 | 42496 | A600 | 3 |  | 256 |  | 512 | Data area of Node 6 |  |  |  | Read
| 82753 | 42752 | A700 | 3 |  | 256 |  | 512 | Data area of Node 7 |  |  |  | Read
| 83009 | 43008 | A800 | 3 |  | 256 |  | 512 | Data area of Node 8 |  |  |  | Read
| 83265 | 43264 | A900 | 3 |  | 256 |  | 512 | Data area of Node 9 |  |  |  | Read
| 83521 | 43520 | AA00 | 3 |  | 256 |  | 512 | Data area of Node 10 |  |  |  | Read
| 85313 | 45312 | B100 | 3 |  | 256 |  | 512 | Data area of Node 11 |  |  |  | Read
| 85569 | 45568 | B200 | 3 |  | 256 |  | 512 | Data area of Node 12 |  |  |  | Read
| 85825 | 45824 | B300 | 3 |  | 256 |  | 512 | Data area of Node 13 |  |  |  | Read
| 86081 | 46080 | B400 | 3 |  | 256 |  | 512 | Data area of Node 14 |  |  |  | Read
| 86337 | 46336 | B500 | 3 |  | 256 |  | 512 | Data area of Node 15 |  |  |  | Read
| 86593 | 46592 | B600 | 3 |  | 256 |  | 512 | Data area of Node 16 |  |  |  | Read
| 86849 | 46848 | B700 | 3 |  | 256 |  | 512 | Data area of Node 17 |  |  |  | Read
| 87105 | 47104 | B800 | 3 |  | 256 |  | 512 | Data area of Node 18 |  |  |  | Read
| 87361 | 47360 | B900 | 3 |  | 256 |  | 512 | Data area of Node 19 |  |  |  | Read
| 87617 | 47616 | BA00 | 3 |  | 256 |  | 512 | Data area of Node 20 |  |  |  | Read
| 89409 | 49408 | C100 | 3 |  | 256 |  | 512 | Data area of Node 21 |  |  |  | Read
| 89665 | 49664 | C200 | 3 |  | 256 |  | 512 | Data area of Node 22 |  |  |  | Read
| 89921 | 49920 | C300 | 3 |  | 256 |  | 512 | Data area of Node 23 |  |  |  | Read
| 90177 | 50176 | C400 | 3 |  | 256 |  | 512 | Data area of Node 24 |  |  |  | Read
| 90433 | 50432 | C500 | 3 |  | 256 |  | 512 | Data area of Node 25 |  |  |  | Read
| 90689 | 50688 | C600 | 3 |  | 256 |  | 512 | Data area of Node 26 |  |  |  | Read
| 90945 | 50944 | C700 | 3 |  | 256 |  | 512 | Data area of Node 27 |  |  |  | Read
| 91201 | 51200 | C800 | 3 |  | 256 |  | 512 | Data area of Node 28 |  |  |  | Read
| 91457 | 51456 | C900 | 3 |  | 256 |  | 512 | Data area of Node 29 |  |  |  | Read
| 91713 | 51712 | CA00 | 3 |  | 256 |  | 512 | Data area of Node 30 |  |  |  | Read
| 93505 | 53504 | D100 | 3 |  | 256 |  | 512 | Data area of Node 31 |  |  |  | Read
| 93761 | 53760 | D200 | 3 |  | 256 |  | 512 | Data area of Node 32 |  |  |  | Read
| 94017 | 54016 | D300 | 3 |  | 256 |  | 512 | Data area of Node 33 |  |  |  | Read
| 94273 | 54272 | D400 | 3 |  | 256 |  | 512 | Data area of Node 34 |  |  |  | Read
| 94529 | 54528 | D500 | 3 |  | 256 |  | 512 | Data area of Node 35 |  |  |  | Read
| 94785 | 54784 | D600 | 3 |  | 256 |  | 512 | Data area of Node 36 |  |  |  | Read
| 95041 | 55040 | D700 | 3 |  | 256 |  | 512 | Data area of Node 37 |  |  |  | Read
| 95297 | 55296 | D800 | 3 |  | 256 |  | 512 | Data area of Node 38 |  |  |  | Read
| 95553 | 55552 | D900 | 3 |  | 256 |  | 512 | Data area of Node 39 |  |  |  | Read
| 95809 | 55808 | DA00 | 3 |  | 256 |  | 512 | Data area of Node 40 |  |  |  | Read
STATUS DATA OF 40 WIRELESS SENSORS | 40009 | 8 | 8 | 3 |  | 20 | 16 | 40 | Rssi node 1..40 |  |  | byte | Read | Only for manuafacture. Raw RSSI value (right number must subtract 256, Unit is dBm).
| 40029 | 28 | 1C | 3 |  | 1 | 56 | 2 | Data status node 1 & Data status node 2 | 0-9, 99 |  | byte | Read | Hi-byte for node 1 & lo-byte for node 2. Details in sheet of sensor
| 40030 | 29 | 1D | 3 |  | 1 | 58 | 2 | Data status node 3 & Data status node 4 | 0-9, 99 |  | byte | Read
| 40031 | 30 | 1E | 3 |  | 1 | 60 | 2 | Data status node 5 & Data status node 6 | 0-9, 99 |  | byte | Read
| 40032 | 31 | 1F | 3 |  | 1 | 62 | 2 | Data status node 7 & Data status node 8 | 0-9, 99 |  | byte | Read
| 40033 | 32 | 20 | 3 |  | 1 | 64 | 2 | Data status node 9 & Data status node 10 | 0-9, 99 |  | byte | Read
| 40034 | 33 | 21 | 3 |  | 1 | 66 | 2 | Data status node 11 & Data status node 12 | 0-9, 99 |  | byte | Read
| 40035 | 34 | 22 | 3 |  | 1 | 68 | 2 | Data status node 13 & Data status node 14 | 0-9, 99 |  | byte | Read
| 40036 | 35 | 23 | 3 |  | 1 | 70 | 2 | Data status node 15 & Data status node 16 | 0-9, 99 |  | byte | Read
| 40037 | 36 | 24 | 3 |  | 1 | 72 | 2 | Data status node 17 & Data status node 18 | 0-9, 99 |  | byte | Read
| 40038 | 37 | 25 | 3 |  | 1 | 74 | 2 | Data status node 19 & Data status node 20 | 0-9, 99 |  | byte | Read
| 40039 | 38 | 26 | 3 |  | 1 | 76 | 2 | Data status node 21 & Data status node 22 | 0-9, 99 |  | byte | Read
| 40040 | 39 | 27 | 3 |  | 1 | 78 | 2 | Data status node 23 & Data status node 24 | 0-9, 99 |  | byte | Read
| 40041 | 40 | 28 | 3 |  | 1 | 80 | 2 | Data status node 25 & Data status node 26 | 0-9, 99 |  | byte | Read
| 40042 | 41 | 29 | 3 |  | 1 | 82 | 2 | Data status node 27 & Data status node 28 | 0-9, 99 |  | byte | Read
| 40043 | 42 | 2A | 3 |  | 1 | 84 | 2 | Data status node 29 & Data status node 30 | 0-9, 99 |  | byte | Read
| 40044 | 43 | 2B | 3 |  | 1 | 86 | 2 | Data status node 31 & Data status node 32 | 0-9, 99 |  | byte | Read
| 40045 | 44 | 2C | 3 |  | 1 | 88 | 2 | Data status node 33 & Data status node 34 | 0-9, 99 |  | byte | Read
| 40046 | 45 | 2D | 3 |  | 1 | 90 | 2 | Data status node 35 & Data status node 36 | 0-9, 99 |  | byte | Read
| 40047 | 46 | 2E | 3 |  | 1 | 92 | 2 | Data status node 37 & Data status node 38 | 0-9, 99 |  | byte | Read
| 40048 | 47 | 2F | 3 |  | 1 | 94 | 2 | Data status node 39 & Data status node 40 | 0-9, 99 |  | byte | Read
| 40049 | 48 | 30 | 3 |  | 20 | 96 | 40 | RF timeout count node 1..40 | 0-255 |  | byte | Read | Counting the number of times that no data from wireless sensor arrived over "timeout_count_threshold" seconds , for ADVANCED diagnostic the RF connection between wireless sensor and co-ordinator
| 40069 | 68 | 44 | 3 |  | 1 | 136 | 2 | RF signal strength of node 1 & RF signal strength of node 2 | 0-4 |  | byte | Read | Hi-byte for node 1 & lo-byte for node 2. Details in sheet of sensor
| 40070 | 69 | 45 | 3 |  | 1 | 138 | 2 | RF signal strength of node 3 & RF signal strength of node 4 | 0-4 |  | byte | Read
| 40071 | 70 | 46 | 3 |  | 1 | 140 | 2 | RF signal strength of node 5 & RF signal strength of node 6 | 0-4 |  | byte | Read
| 40072 | 71 | 47 | 3 |  | 1 | 142 | 2 | RF signal strength of node 7 & RF signal strength of node 8 | 0-4 |  | byte | Read
| 40073 | 72 | 48 | 3 |  | 1 | 144 | 2 | RF signal strength of node 9 & RF signal strength of node 10 | 0-4 |  | byte | Read
| 40074 | 73 | 49 | 3 |  | 1 | 146 | 2 | RF signal strength of node 11 & RF signal strength of node 12 | 0-4 |  | byte | Read
| 40075 | 74 | 4A | 3 |  | 1 | 148 | 2 | RF signal strength of node 13 & RF signal strength of node 14 | 0-4 |  | byte | Read
| 40076 | 75 | 4B | 3 |  | 1 | 150 | 2 | RF signal strength of node 15 & RF signal strength of node 16 | 0-4 |  | byte | Read
| 40077 | 76 | 4C | 3 |  | 1 | 152 | 2 | RF signal strength of node 17 & RF signal strength of node 18 | 0-4 |  | byte | Read
| 40078 | 77 | 4D | 3 |  | 1 | 154 | 2 | RF signal strength of node 19 & RF signal strength of node 20 | 0-4 |  | byte | Read
| 40079 | 78 | 4E | 3 |  | 1 | 156 | 2 | RF signal strength of node 21 & RF signal strength of node 22 | 0-4 |  | byte | Read
| 40080 | 79 | 4F | 3 |  | 1 | 158 | 2 | RF signal strength of node 23 & RF signal strength of node 24 | 0-4 |  | byte | Read
| 40081 | 80 | 50 | 3 |  | 1 | 160 | 2 | RF signal strength of node 25 & RF signal strength of node 26 | 0-4 |  | byte | Read
| 40082 | 81 | 51 | 3 |  | 1 | 162 | 2 | RF signal strength of node 27 & RF signal strength of node 28 | 0-4 |  | byte | Read
| 40083 | 82 | 52 | 3 |  | 1 | 164 | 2 | RF signal strength of node 29 & RF signal strength of node 30 | 0-4 |  | byte | Read
| 40084 | 83 | 53 | 3 |  | 1 | 166 | 2 | RF signal strength of node 31 & RF signal strength of node 32 | 0-4 |  | byte | Read
| 40085 | 84 | 54 | 3 |  | 1 | 168 | 2 | RF signal strength of node 33 & RF signal strength of node 34 | 0-4 |  | byte | Read
| 40086 | 85 | 55 | 3 |  | 1 | 170 | 2 | RF signal strength of node 35 & RF signal strength of node 36 | 0-4 |  | byte | Read
| 40087 | 86 | 56 | 3 |  | 1 | 172 | 2 | RF signal strength of node 37 & RF signal strength of node 38 | 0-4 |  | byte | Read
| 40088 | 87 | 57 | 3 |  | 1 | 174 | 2 | RF signal strength of node 39 & RF signal strength of node 40 | 0-4 |  | byte | Read
| 40089 | 88 | 58 | 3 |  | 60 | 176 | 120 | spare |  |  | byte | Read
| 40149 | 148 | 94 | 3 |  | 20 | 296 | 40 | Rx seq node 1..40 | 0-255 |  | byte | Read | Only for manuafacture. Sequence number of data package, value from wireless sensor, for ADVANCED diagnostic of RF connecttion, to know lost of data package from sensor to Co-ordinator
| 40169 | 168 | A8 | 3 |  | 20 | 336 | 40 | Rx duplication count node 1..40 | 0-255 |  | byte | Read | For manuafacture. Counting the number of Dupplicated data package from sensor, to define that sensor have not received the ACK package from Co-ordinator
| 40189 | 188 | BC | 3 |  | 1 | 376 | 2 | Sync status node 1 & Sync status node 2 | 0, 1, 99 |  | byte | Read | Hi-byte for node 1 & lo-byte for node 2. Details in sheet of sensor
| 40190 | 189 | BD | 3 |  | 1 | 378 | 2 | Sync status node 3 & Sync status node 4 | 0, 1, 99 |  | byte | Read
| 40191 | 190 | BE | 3 |  | 1 | 380 | 2 | Sync status node 5 & Sync status node 6 | 0, 1, 99 |  | byte | Read
| 40192 | 191 | BF | 3 |  | 1 | 382 | 2 | Sync status node 7 & Sync status node 8 | 0, 1, 99 |  | byte | Read
| 40193 | 192 | C0 | 3 |  | 1 | 384 | 2 | Sync status node 9 & Sync status node 10 | 0, 1, 99 |  | byte | Read
| 40194 | 193 | C1 | 3 |  | 1 | 386 | 2 | Sync status node 11 & Sync status node 12 | 0, 1, 99 |  | byte | Read
| 40195 | 194 | C2 | 3 |  | 1 | 388 | 2 | Sync status node 13 & Sync status node 14 | 0, 1, 99 |  | byte | Read
| 40196 | 195 | C3 | 3 |  | 1 | 390 | 2 | Sync status node 15 & Sync status node 16 | 0, 1, 99 |  | byte | Read
| 40197 | 196 | C4 | 3 |  | 1 | 392 | 2 | Sync status node 17 & Sync status node 18 | 0, 1, 99 |  | byte | Read
| 40198 | 197 | C5 | 3 |  | 1 | 394 | 2 | Sync status node 19 & Sync status node 20 | 0, 1, 99 |  | byte | Read
| 40199 | 198 | C6 | 3 |  | 1 | 396 | 2 | Sync status node 21 & Sync status node 22 | 0, 1, 99 |  | byte | Read
| 40200 | 199 | C7 | 3 |  | 1 | 398 | 2 | Sync status node 23 & Sync status node 24 | 0, 1, 99 |  | byte | Read
| 40201 | 200 | C8 | 3 |  | 1 | 400 | 2 | Sync status node 25 & Sync status node 26 | 0, 1, 99 |  | byte | Read
| 40202 | 201 | C9 | 3 |  | 1 | 402 | 2 | Sync status node 27 & Sync status node 28 | 0, 1, 99 |  | byte | Read
| 40203 | 202 | CA | 3 |  | 1 | 404 | 2 | Sync status node 29 & Sync status node 30 | 0, 1, 99 |  | byte | Read
| 40204 | 203 | CB | 3 |  | 1 | 406 | 2 | Sync status node 31 & Sync status node 32 | 0, 1, 99 |  | byte | Read
| 40205 | 204 | CC | 3 |  | 1 | 408 | 2 | Sync status node 33 & Sync status node 34 | 0, 1, 99 |  | byte | Read
| 40206 | 205 | CD | 3 |  | 1 | 410 | 2 | Sync status node 35 & Sync status node 36 | 0, 1, 99 |  | byte | Read
| 40207 | 206 | CE | 3 |  | 1 | 412 | 2 | Sync status node 37 & Sync status node 38 | 0, 1, 99 |  | byte | Read
| 40208 | 207 | CF | 3 |  | 1 | 414 | 2 | Sync status node 39 & Sync status node 40 | 0, 1, 99 |  | byte | Read
CONTROL DATA OF 40 WIRELESS SENSORS | 42001 | 2000 | 7D0 | 3 | 16 | 8 |  | 16 | Control area of node 1 |  |  |  | Read/Write | Control area for each wireless sensor, see details in sheet of sensor
| 42009 | 2008 | 7D8 | 3 | 16 | 8 |  | 16 | Control area of node 2 |  |  |  | Read/Write
| 42017 | 2016 | 7E0 | 3 | 16 | 8 |  | 16 | Control area of node 3 |  |  |  | Read/Write
| 42025 | 2024 | 7E8 | 3 | 16 | 8 |  | 16 | Control area of node 4 |  |  |  | Read/Write
| 42033 | 2032 | 7F0 | 3 | 16 | 8 |  | 16 | Control area of node 5 |  |  |  | Read/Write
| 42041 | 2040 | 7F8 | 3 | 16 | 8 |  | 16 | Control area of node 6 |  |  |  | Read/Write
| 42049 | 2048 | 800 | 3 | 16 | 8 |  | 16 | Control area of node 7 |  |  |  | Read/Write
| 42057 | 2056 | 808 | 3 | 16 | 8 |  | 16 | Control area of node 8 |  |  |  | Read/Write
| 42065 | 2064 | 810 | 3 | 16 | 8 |  | 16 | Control area of node 9 |  |  |  | Read/Write
| 42073 | 2072 | 818 | 3 | 16 | 8 |  | 16 | Control area of node 10 |  |  |  | Read/Write
| 42081 | 2080 | 820 | 3 | 16 | 8 |  | 16 | Control area of node 11 |  |  |  | Read/Write
| 42089 | 2088 | 828 | 3 | 16 | 8 |  | 16 | Control area of node 12 |  |  |  | Read/Write
| 42097 | 2096 | 830 | 3 | 16 | 8 |  | 16 | Control area of node 13 |  |  |  | Read/Write
| 42105 | 2104 | 838 | 3 | 16 | 8 |  | 16 | Control area of node 14 |  |  |  | Read/Write
| 42113 | 2112 | 840 | 3 | 16 | 8 |  | 16 | Control area of node 15 |  |  |  | Read/Write
| 42121 | 2120 | 848 | 3 | 16 | 8 |  | 16 | Control area of node 16 |  |  |  | Read/Write
| 42129 | 2128 | 850 | 3 | 16 | 8 |  | 16 | Control area of node 17 |  |  |  | Read/Write
| 42137 | 2136 | 858 | 3 | 16 | 8 |  | 16 | Control area of node 18 |  |  |  | Read/Write
| 42145 | 2144 | 860 | 3 | 16 | 8 |  | 16 | Control area of node 19 |  |  |  | Read/Write
| 42153 | 2152 | 868 | 3 | 16 | 8 |  | 16 | Control area of node 20 |  |  |  | Read/Write
| 42161 | 2160 | 870 | 3 | 16 | 8 |  | 16 | Control area of node 21 |  |  |  | Read/Write
| 42169 | 2168 | 878 | 3 | 16 | 8 |  | 16 | Control area of node 22 |  |  |  | Read/Write
| 42177 | 2176 | 880 | 3 | 16 | 8 |  | 16 | Control area of node 23 |  |  |  | Read/Write
| 42185 | 2184 | 888 | 3 | 16 | 8 |  | 16 | Control area of node 24 |  |  |  | Read/Write
| 42193 | 2192 | 890 | 3 | 16 | 8 |  | 16 | Control area of node 25 |  |  |  | Read/Write
| 42201 | 2200 | 898 | 3 | 16 | 8 |  | 16 | Control area of node 26 |  |  |  | Read/Write
| 42209 | 2208 | 8A0 | 3 | 16 | 8 |  | 16 | Control area of node 27 |  |  |  | Read/Write
| 42217 | 2216 | 8A8 | 3 | 16 | 8 |  | 16 | Control area of node 28 |  |  |  | Read/Write
| 42225 | 2224 | 8B0 | 3 | 16 | 8 |  | 16 | Control area of node 29 |  |  |  | Read/Write
| 42233 | 2232 | 8B8 | 3 | 16 | 8 |  | 16 | Control area of node 30 |  |  |  | Read/Write
| 42241 | 2240 | 8C0 | 3 | 16 | 8 |  | 16 | Control area of node 31 |  |  |  | Read/Write
| 42249 | 2248 | 8C8 | 3 | 16 | 8 |  | 16 | Control area of node 32 |  |  |  | Read/Write
| 42257 | 2256 | 8D0 | 3 | 16 | 8 |  | 16 | Control area of node 33 |  |  |  | Read/Write
| 42265 | 2264 | 8D8 | 3 | 16 | 8 |  | 16 | Control area of node 34 |  |  |  | Read/Write
| 42273 | 2272 | 8E0 | 3 | 16 | 8 |  | 16 | Control area of node 35 |  |  |  | Read/Write
| 42281 | 2280 | 8E8 | 3 | 16 | 8 |  | 16 | Control area of node 36 |  |  |  | Read/Write
| 42289 | 2288 | 8F0 | 3 | 16 | 8 |  | 16 | Control area of node 37 |  |  |  | Read/Write
| 42297 | 2296 | 8F8 | 3 | 16 | 8 |  | 16 | Control area of node 38 |  |  |  | Read/Write
| 42305 | 2304 | 900 | 3 | 16 | 8 |  | 16 | Control area of node 39 |  |  |  | Read/Write
| 42313 | 2312 | 908 | 3 | 16 | 8 |  | 16 | Control area of node 40 |  |  |  | Read/Write
SYSTEM CONFIG | 40260 | 259 | 103 | 3 | 16 | 9 | 6 | 18 | Serial number |  |  | string | Read/Write(PW) | Only for manuafacture. Serial number of Wireless sensor co-ordinator.
| 40269 | 268 | 10C | 3 | 16 | 2 | 24 | 4 | Password for setting |  |  | uint32 | Read/Write | Password for writing co-ordinator S/N and ID.
| 40271 | 270 | 10E | 3 | 16 | 2 | 28 | 4 | Co-ordinator id |  |  | uint32 | Read/Write(PW) | Only for manuafacture. The ID number of Wireless sensor co-ordinator.
ADVANCED CONFIG | 40401 | 400 | 190 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 1 |  |  |  | Read/Write | Configuration data area for each wireless sensor, see details in sheet of sensor
| 40441 | 440 | 1B8 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 2 |  |  |  | Read/Write
| 40481 | 480 | 1E0 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 3 |  |  |  | Read/Write
| 40521 | 520 | 208 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 4 |  |  |  | Read/Write
| 40561 | 560 | 230 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 5 |  |  |  | Read/Write
| 40601 | 600 | 258 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 6 |  |  |  | Read/Write
| 40641 | 640 | 280 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 7 |  |  |  | Read/Write
| 40681 | 680 | 2A8 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 8 |  |  |  | Read/Write
| 40721 | 720 | 2D0 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 9 |  |  |  | Read/Write
| 40761 | 760 | 2F8 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 10 |  |  |  | Read/Write
| 40801 | 800 | 320 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 11 |  |  |  | Read/Write
| 40841 | 840 | 348 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 12 |  |  |  | Read/Write
| 40881 | 880 | 370 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 13 |  |  |  | Read/Write
| 40921 | 920 | 398 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 14 |  |  |  | Read/Write
| 40961 | 960 | 3C0 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 15 |  |  |  | Read/Write
| 41001 | 1000 | 3E8 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 16 |  |  |  | Read/Write
| 41041 | 1040 | 410 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 17 |  |  |  | Read/Write
| 41081 | 1080 | 438 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 18 |  |  |  | Read/Write
| 41121 | 1120 | 460 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 19 |  |  |  | Read/Write
| 41161 | 1160 | 488 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 20 |  |  |  | Read/Write
| 41201 | 1200 | 4B0 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 21 |  |  |  | Read/Write
| 41241 | 1240 | 4D8 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 22 |  |  |  | Read/Write
| 41281 | 1280 | 500 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 23 |  |  |  | Read/Write
| 41321 | 1320 | 528 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 24 |  |  |  | Read/Write
| 41361 | 1360 | 550 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 25 |  |  |  | Read/Write
| 41401 | 1400 | 578 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 26 |  |  |  | Read/Write
| 41441 | 1440 | 5A0 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 27 |  |  |  | Read/Write
| 41481 | 1480 | 5C8 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 28 |  |  |  | Read/Write
| 41521 | 1520 | 5F0 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 29 |  |  |  | Read/Write
| 41561 | 1560 | 618 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 30 |  |  |  | Read/Write
| 41601 | 1600 | 640 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 31 |  |  |  | Read/Write
| 41641 | 1640 | 668 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 32 |  |  |  | Read/Write
| 41681 | 1680 | 690 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 33 |  |  |  | Read/Write
| 41721 | 1720 | 6B8 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 34 |  |  |  | Read/Write
| 41761 | 1760 | 6E0 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 35 |  |  |  | Read/Write
| 41801 | 1800 | 708 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 36 |  |  |  | Read/Write
| 41841 | 1840 | 730 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 37 |  |  |  | Read/Write
| 41881 | 1880 | 758 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 38 |  |  |  | Read/Write
| 41921 | 1920 | 780 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 39 |  |  |  | Read/Write
| 41961 | 1960 | 7A8 | 3 | 16 | 40 | #REF! | 80 | Configuration of node 40 |  |  |  | Read/Write
SETTING TIMEOUT VALUE OF DATA STATUS | 40354 | 353 | 161 | 3 | 16 | 1 | 194 | 2 | Cmp time 1 |  | 15 | uint16 | Read/Write | Time interval for Data status = 0
| 40355 | 354 | 162 | 3 | 16 | 1 | 196 | 2 | Cmp time 2 |  | 30 | uint16 | Read/Write | Time interval for Data status = 1
| 40356 | 355 | 163 | 3 | 16 | 1 | 198 | 2 | Cmp time 3 |  | 45 | uint16 | Read/Write | Time interval for Data status = 2
| 40357 | 356 | 164 | 3 | 16 | 1 | 200 | 2 | Cmp time 4 |  | 60 | uint16 | Read/Write | Time interval for Data status = 3
| 40358 | 357 | 165 | 3 | 16 | 1 | 202 | 2 | Cmp time 5 |  | 300 | uint16 | Read/Write | Time interval for Data status = 4
| 40359 | 358 | 166 | 3 | 16 | 1 | 204 | 2 | Cmp time 6 |  | 600 | uint16 | Read/Write | Time interval for Data status = 5
| 40360 | 359 | 167 | 3 | 16 | 1 | 206 | 2 | Cmp time 7 |  | 900 | uint16 | Read/Write | Time interval for Data status = 6
| 40361 | 360 | 168 | 3 | 16 | 1 | 208 | 2 | Cmp time 8 |  | 1800 | uint16 | Read/Write | Time interval for Data status = 7
| 40362 | 361 | 169 | 3 | 16 | 1 | 210 | 2 | Cmp time 9 |  | 3600 | uint16 | Read/Write | Time interval for Data status = 8
SETTING TIMEOUT VALUE OF RF TIMEOUT COUNT | 40363 | 362 | 16A | 16 |  | 1 | 212 | 2 | Timeout_count_threshold |  | 630 | uint16 | Read/Write | Time interval for Rf_timeout_count increase one more
RF MODE CONFIG | 40364 | 363 | 16B | 3 | 16 | 2 | 214 | 4 | Radio frequency | 433.05-434.79, 433 MHz | 433.92 | float | Read/Write | Only for advanced users. Configure the operating frequency of Co-ordinator, should be configured from 433.05-434.79 MHz.
| 40366 | 365 | 16D | 3 | 16 | 1 | 218 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Only for advanced users. Configure the RF power of Co-ordinator + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm
| 40367 | 366 | 16E | 3 | 16 | 1 | 220 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Only for advanced users. Configure the air data rate of Co-ordinator + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps
| 40368 | 367 | 16F | 3 | 16 | 1 | 218 | 2 | Rssi_threshold | -100…0 | -25 | int16 | Read/Write | RSSI value, this is the threshold to allow adding wireless sensors by RF when the rssi value is higher than the rssi_threshold. Should be configured from -14dBm to -40 dBm
| 40369 | 368 | 170 | 3 | 16 | 1 | 218 | 2 | Enb_auto_add_sensors | 0-1 | 0 | uint16 | Read/Write | "Enb_auto_add_sensors" = 1 when power on and this parameter will return to "0" after 5 minutes: + 1 => allow adding wireless sensors by RF + 0 => not allow adding wireless sensors by RF Write "Enb_auto_add_sensors" = 1 => this parameter will return to "0" after 5 minutes
| 40369 | 368 | 170 | 16 |  | 32 | 214 | 64 | Spare |  |  |  | Read/Write
DEVICE INFO | 40001 | 0 | 0 | 3 |  | 2 | 0 | 4 | Device info |  | WSCL | string | Read | Wireless sensor co-ordinator
| 40003 | 2 | 2 | 3 |  | 4 | 4 | 8 | Firmware version |  | 1.9 | string | Read
| 40007 | 6 | 6 | 3 |  | 2 | 12 | 4 | Hardware version |  | 2.4 | string | Read

## Memmap of WS433-M12F and ATE
MODBUS MEMORY MAP FOR WIRELESS TEMPERATURE SENSOR WS433-M12F WITH ATE-xx
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 1) | -40..+125oC |  | float | Read | Value from temperature sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | Same value as parameter 1 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-M12F and PT100
MODBUS MEMORY MAP FOR WIRELESS RTD PT100 SENSOR WS433-M12F WITH PT100
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | PT100 Temperature value of sensor Node (parameter 1) | -200..750oC |  | float | Read | Value from RTD PT100 sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | PT100 Resistance value of sensor Node (parameter 2) | 18..360 ohm |  | float | Read | Value from RTD PT100 sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-M12F and ATH
MODBUS MEMORY MAP FOR WIRELESS HUMIDITY SENSOR WS433-M12F WITH ATH
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Humidity value of sensor Node (parameter 1) | 0..100% |  | float | Read | Value from humidity sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from humidity sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-M12F and ADP
MODBUS MEMORY MAP FOR WIRELESS DIFFERENTIAL PRESSURE SENSOR WS433-M12F WITH ADP
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Differential Pressure value of sensor Node (parameter 1) | -125..+125Pa |  | float | Read | Value from differential pressure sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from differential pressure sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-M12F and PPS
MODBUS MEMORY MAP FOR WIRELESS PRESSURE SENSOR WS433-M12F WITH PPS
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Pressure value of sensor Node (parameter 1) | 0..100% |  | float | Read | Value from pressure process sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node (parameter 2) |  |  | float | Read | Value from pressure process sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-M12F and ALS
MODBUS MEMORY MAP FOR WIRELESS DIFFERENTIAL PRESSURE SENSOR WS433-M12F WITH AMBIENT LIGHT SENSOR
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | illuminance value of sensor Node (parameter 1) | 20.48..+83865.6 |  | float | Read | Value from ambient light sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | Same value as parameter 1 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-AC
MODBUS MEMORY MAP FOR WIRELESS AC CURRENT SENSOR WS433-AC
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | AC Current value of sensor Node (parameter 1) | A |  | float | Read | Value from ac current sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | Same value as parameter 1 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | CT_factor |  | 40 | float | Read/Write | CT factor value of Current Transformer | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 2 | 4 | Cutoff_current |  | 0.5 | float | Read/Write | Cut-off current value, this is the threshold to force ac current value = 0 when the load current is less then the threshold | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 7 | 14 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-DI and Status
MODBUS MEMORY MAP FOR WIRELESS DIGITAL INPUT SENSOR WS433-DI WITH 2 STATUS INPUT
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 1 | 2 | Digital status 1 of sensor Node (parameter 1) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value is parameter 1 of a wireless sensor node
| 30003 | 2 | 2 | 4 |  | 1 | 2 | Digital status 2 of sensor Node (parameter 2) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value is parameter 2 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 1 | 2 | Digital toggle 1 of sensor Node (parameter 1) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value will toggle when detecting rising-edge
| 30006 | 5 | 5 | 4 |  | 1 | 2 | Digital toggle 2 of sensor Node (parameter 2) | 0-1 |  | uint16 | Read | Value from digital input sensor. This value will toggle when detecting rising-edge | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Not Applicable. Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | Counter value 1 | 0-999,999,999 |  | uint32 | Read/Write | Not Applicable. This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 2 | 4 | Counter value 2 | 0-999,999,999 |  | uint32 | Read/Write | Not Applicable. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 1 | 2 | Pulse width 1 |  | 90 | uint16 | Read/Write | Pulse width value for the digital input 1, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 1 | 2 | Pulse width 2 |  | 90 | uint16 | Read/Write | Pulse width value for the digital input 2, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | 5 | 10 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-DI and Counter
MODBUS MEMORY MAP FOR WIRELESS DIGITAL INPUT SENSOR WS433-DI WITH 2 COUNTER INPUT
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Counter value 1 of sensor Node (parameter 1) | 0-999,999,999 |  | uint32 | Read | Value from digital input sensor. This value is parameter 1 of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Counter value 2 of sensor Node (parameter 2) | 0-999,999,999 |  | uint32 | Read | Value from digital input sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Not Applicable. Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Not Applicable. Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Not Applicable. Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Not Applicable. Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Not Applicable. Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Not Applicable. Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Not Applicable. Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Not Applicable. Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | Counter value 1 | 0-999,999,999 |  | uint32 | Read/Write | This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 2 | 4 | Counter value 2 | 0-999,999,999 |  | uint32 | Read/Write | This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 1 | 2 | Pulse width 1 |  | 90 | uint16 | Read/Write | Pulse width value for the digital input 1, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 1 | 2 | Pulse width 2 |  | 90 | uint16 | Read/Write | Pulse width value for the digital input 2, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | 5 | 10 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-RL
MODBUS MEMORY MAP FOR WIRELESS RELAY OUTPUT SENSOR WS433-RL
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
Control Data * This control data will sent to sensor node immediately | 42001 | 2000 | 7D0 | 3 | 16 | 1 | 2 | Control Relay 1 of sensor Node | 0-1 | 0 | uint16 | Read/Write | 0: turn off relay 1 1: turn on relay 1
| 42002 | 2001 | 7D1 | 3 | 16 | 1 | 2 | Control Relay 2 of sensor Node | 0-1 | 0 | uint16 | Read/Write | 0: turn off relay 2 1: turn on relay 2
| 42003 | 2002 | 7D2 | 3 | 16 | 1 | 2 | Control Relay 3 of sensor Node | 0-1 | 0 | uint16 | Read/Write | 0: turn off relay 3 1: turn on relay 3
| 42004 | 2003 | 7D3 | 3 | 16 | 1 | 2 | Control Relay 4 of sensor Node | 0-1 | 0 | uint16 | Read/Write | 0: turn off relay 4 1: turn on relay 4
| 42005 | 2004 | 7D4 | 3 | 16 | (5): 4; (6): 8; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (12): Not Applicable
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Not Applicable. Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 1 | 2 | Status Relay 1 of sensor Node |  |  | uint16 | Read | Value from relay output sensor, this value is status of relay 1 for a wireless sensor node
| 30003 | 2 | 2 | 4 |  | 1 | 2 | Status Relay 2 of sensor Node |  |  | uint16 | Read | Value from relay output sensor, this value is status of relay 2 for a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 1 | 2 | Status Relay 3 of sensor Node |  |  | uint16 | Read | Value from relay output sensor, this value is status of relay 3 for a wireless sensor node
| 30006 | 5 | 5 | 4 |  | 1 | 2 | Status Relay 4 of sensor Node |  |  | uint16 | Read | Value from relay output sensor, this value is status of relay 4 for a wireless sensor node | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Not Applicable. Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Not Applicable. Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Not Applicable. Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Not Applicable. Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Not Applicable. Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Not Applicable. Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Not Applicable. Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Not Applicable. Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 |  | 2 | 4 | a1 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 |  | 2 | 4 | b1 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Not Applicable. Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | Default relay 1 | 0-2 | 0 | uint16 | Read/Write | 0: off, 1: on, 2: last state (Restores the previous power state before power loss occurs) | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | Default relay 2 | 0-2 | 0 | uint16 | Read/Write | 0: off, 1: on, 2: last state (Restores the previous power state before power loss occurs) | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 1 | 2 | Default relay 3 | 0-2 | 0 | uint16 | Read/Write | 0: off, 1: on, 2: last state (Restores the previous power state before power loss occurs) | for sensor with V5.x
| 40430 | 429 | 1AD | 3 | 16 | 1 | 2 | Default relay 4 | 0-2 | 0 | uint16 | Read/Write | 0: off, 1: on, 2: last state (Restores the previous power state before power loss occurs) | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 7 | 14 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-AI
MODBUS MEMORY MAP FOR WIRELESS ANALOG INPUT SENSOR WS433-AI
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 2 | 4 | Analog value 1 of sensor Node (parameter 1) |  |  | float | Read | Value from Analog input sensor. This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Value of parameter 2 of sensor Node |  |  | float | Read | Same value as parameter 1 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | Response_time | ms | 0 | uint16 | Read/Write | Actual times for Field Instruments to output data. This value will vary dependent on Field Instruments | for sensor with V5.x
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | Response_time_max | 100-65535 ms | 3000 | uint16 | Read/Write | This is the maximum preset value for response time | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 1 | 2 | Run_mode | 0-1 | 0 | uint16 | Read/Write | "Run_mode" = 1 when power on and this parameter will return to "0" after 5 cycles send data to co-ordinator: + 1 => allow auto-detect response time after some cycle send data to co-ordinator + 0 => stop auto-detect response time Write "Run_mode" = 1 => this parameter will return to "0" after 5 cycles send data to co-ordinator | for sensor with V5.x
| 40430 | 429 | 1AD | 3 | 16 | 2 | 4 | Cutoff |  | 0 | float | Read/Write | Cut-off value, this is the threshold to force Analog value 1 of sensor Node = 0 when it is less then the threshold | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 6 | 12 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-SOIL MOISTURE
MODBUS MEMORY MAP FOR WIRELESS SOIL MOISTURE - E.C - TEMPERATURE SENSOR
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 1 | 2 | Soil moisture of sensor Node (parameter 1) | 0-1000 (‰) |  | uint16 | Read | Value from soil moisture sensor. This value is parameter 1 of a wireless sensor node | for sensor with V5.x
| 30003 | 2 | 2 | 4 |  | 1 | 2 | E.C of sensor Node (parameter 2) | 0-2000 (mS/m) |  | uint16 | Read | Value from soil moisture sensor. This value is parameter 2 of a wireless sensor node | for sensor with V5.x
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 2 | 4 | Temperature value of sensor Node | -30oC…+70oC |  | float | Read | Value from soil moisture sensor | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Logic status of parameters |  |  | uint16 | Read | Hi-Byte is Logic status of parameter 1, Lo-Byte is Logic status of parameter 2 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 2 | 4 | Timer up 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 1 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 2 | 4 | Timer down 1 |  |  | uint32 | Read | Total time when Hi-Byte of Logic status = 0 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 2 | 4 | RisingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 2 | 4 | FallingEdge counter 1 |  |  | uint32 | Read | Counter value when Hi-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
| 30016 | 15 | F | 4 |  | 2 | 4 | Timer up 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 1 | for sensor with V5.x
| 30018 | 17 | 11 | 4 |  | 2 | 4 | Timer down 2 |  |  | uint32 | Read | Total time when Lo-Byte of Logic status = 0 | for sensor with V5.x
| 30020 | 19 | 13 | 4 |  | 2 | 4 | RisingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 0 to 1 | for sensor with V5.x
| 30022 | 21 | 15 | 4 |  | 2 | 4 | FallingEdge counter 2 |  |  | uint32 | Read | Counter value when Lo-Byte of Logic status changes from 1 to 0 | for sensor with V5.x
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_1 |  | 0 | float | Read/Write | Delta value, this is the threshold to allow sending data to co-ordinator when the new value of parameter 1 is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 16 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40429 | 428 | 1AC | 16 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | (5): 1; (6): 2; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | (5): 5; (6): 10; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read/Write; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of WS433-GYRO
MODBUS MEMORY MAP FOR WIRELESS GYRO & ACCELEROMETE SENSOR
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | 1 | 2 | Tilt axis X | -90⁰..+90⁰ |  | int16 | Read | Value from gyro & acceleromete sensor. This value is parameter of a wireless sensor node
| 30003 | 2 | 2 | 4 |  | 1 | 2 | Tilt360 axis X | 0⁰..360⁰ |  | int16 | Read | Value from gyro & acceleromete sensor. This value is parameter of a wireless sensor node
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 1 | 2 | Tilt axis Y | -90⁰..+90⁰ |  | int16 | Read | Value from gyro & acceleromete sensor. This value is parameter of a wireless sensor node
| 30006 | 5 | 5 | 4 |  | 1 | 2 | Tilt360 axis Y | 0⁰..360⁰ |  | int16 | Read | Value from gyro & acceleromete sensor. This value is parameter of a wireless sensor node
| 30007 | 6 | 6 | 4 |  | 1 | 2 | Tilt axis Z | -90⁰..+90⁰ |  | int16 | Read | Value from gyro & acceleromete sensor. This value is parameter of a wireless sensor node
| 30008 | 7 | 7 | 4 |  | 1 | 2 | Tilt360 axis Z | 0⁰..360⁰ |  | int16 | Read | Value from gyro & acceleromete sensor. This value is parameter of a wireless sensor node
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | 2 | 4 | a1 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | 2 | 4 | b1 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_1 = (a1 * Raw sensor value of parameter_1) + b1. For sensor value scale | for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | 2 | 4 | a2 |  | 1 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | 2 | 4 | b2 |  | 0 | float | Read/Write | Not Applicable. Scale value of parameter_2 = (a2 * Raw sensor value of parameter_2) + b2. For sensor value scale | for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | 2 | 4 | Delta_axisX |  | 0 | float | Read/Write | Delta value for Tilt axis X, this is the threshold to allow sending data to co-ordinator when the new value of Tilt axis X is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 2 | 4 | High_threshold_1 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 1 | for sensor with V5.x
| 40421 | 420 | 1A4 | 3 | 16 | 2 | 4 | Low_threshold_1 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 1 | for sensor with V5.x
| 40423 | 422 | 1A6 | 3 | 16 | 2 | 4 | High_threshold_2 |  | 0 | float | Read/Write | Not Applicable. High threshold value for parameter 2 | for sensor with V5.x
| 40425 | 424 | 1A8 | 3 | 16 | 2 | 4 | Low_threshold_2 |  | 0 | float | Read/Write | Not Applicable. Low threshold value for parameter 2 | for sensor with V5.x
| 40427 | 426 | 1AA | 3 | 16 | 2 | 4 | Delta_axisY |  | 0 | float | Read/Write | Delta value for Tilt axis Y, this is the threshold to allow sending data to co-ordinator when the new value of Tilt axis Y is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40429 | 428 | 1AC | 3 | 16 | 2 | 4 | Delta_axisZ |  | 0 | float | Read/Write | Delta value for Tilt axis Z, this is the threshold to allow sending data to co-ordinator when the new value of Tilt axis Z is changed from the last value a delta value which is higher than the threshold. | for sensor with V5.x
| 40431 | 430 | 1AE | 16 |  | 1 | 2 | Pulse width 1 |  | 90 | uint16 | Read/Write | Pulse width value for the digital input 1, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40432 | 431 | 1AF | 16 |  | 1 | 2 | Pulse width 2 |  | 90 | uint16 | Read/Write | Pulse width value for the digital input 2, this is the minimum threshold to allow digital input detect pulse | for sensor with V5.x
| 40433 | 432 | 1B0 | 16 |  | 5 | 10 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40438 | 437 | 1B5 | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40439 | 438 | 1B6 | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40440 | 439 | 1B7 | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x

## Memmap of 1-wire
MODBUS MEMORY MAP FOR WIRELESS TEMPERATURE SENSOR WS433-M12F WITH ATE-xx
Please enter Sensor Node's ID (1 .. 40): | [7 empty] | 1 | to get the correct address of registers in column (1)
* A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte)
| (1) | (2) | (3) | (4) |  | (5) | (6) | (7) | (8) | (9) | (10) | (11) | (12) | (13)
| Modbus Register | Modbus Register (Decimal) | Modbus Register (HEX) | Function Code (Read) | Function Code (Write) | # of register | Byte Size | Description | Value Range | Default | Format | Property | Explanation | Remarks
OPERATION DATA * This operation data will be sent to Co-ordinator in every Cycle_wakeup and/or Cycle_healthsta | 30001 | 0 | 0 | 4 |  | 1 | 2 | %Battery of sensor Node | 10,30,60,99 |  | uint16 | Read | Battery level, only 04 levels: 10%, 30%, 60% and 99% (full). When 10% ==> should replace the battery
| 30002 | 1 | 1 | 4 |  | (5): 2; (6): 4; (7): Spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (10): float; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (11): Read
| 30004 | 3 | 3 | 4 |  | 1 | 2 | Status bytes of sensor Node |  |  | uint16 | Read | Hi-Byte is error code, Lo-Byte is sensor type
| 30005 | 4 | 4 | 4 |  | 1 | 2 | TempC 1 |  |  | int16 | Read | Temperature of 1-wire-sensor 1 | for sensor with V5.x
| 30006 | 5 | 5 | 4 |  | 1 | 2 | TempC 2 |  |  | int16 | Read | Temperature of 1-wire-sensor 2 | for sensor with V5.x
| 30007 | 6 | 6 | 4 |  | 1 | 2 | TempC 3 |  |  | int16 | Read | Temperature of 1-wire-sensor 3 | for sensor with V5.x
| 30008 | 7 | 7 | 4 |  | 1 | 2 | TempC 4 |  |  | int16 | Read | Temperature of 1-wire-sensor 4 | for sensor with V5.x
| 30009 | 8 | 8 | 4 |  | 1 | 2 | TempC 5 |  |  | int16 | Read | Temperature of 1-wire-sensor 5 | for sensor with V5.x
| 30010 | 9 | 9 | 4 |  | 1 | 2 | TempC 6 |  |  | int16 | Read | Temperature of 1-wire-sensor 6 | for sensor with V5.x
| 30011 | 10 | A | 4 |  | 1 | 2 | TempC 7 |  |  | int16 | Read | Temperature of 1-wire-sensor 7 | for sensor with V5.x
| 30012 | 11 | B | 4 |  | 1 | 2 | TempC 8 |  |  | int16 | Read | Temperature of 1-wire-sensor 8 | for sensor with V5.x
| 30013 | 12 | C | 4 |  | 1 | 2 | TempC 9 |  |  | int16 | Read | Temperature of 1-wire-sensor 9 | for sensor with V5.x
| 30014 | 13 | D | 4 |  | 1 | 2 | TempC 10 |  |  | int16 | Read | Temperature of 1-wire-sensor 10
| 30015 | 14 | E | 4 |  | 1 | 2 | TempC 11 |  |  | int16 | Read | Temperature of 1-wire-sensor 11
| 30016 | 15 | F | 4 |  | 1 | 2 | TempC 12 |  |  | int16 | Read | Temperature of 1-wire-sensor 12
| 30017 | 16 | 10 | 4 |  | 1 | 2 | TempC 13 |  |  | int16 | Read | Temperature of 1-wire-sensor 13
| 30018 | 17 | 11 | 4 |  | 1 | 2 | TempC 14 |  |  | int16 | Read | Temperature of 1-wire-sensor 14
| 30019 | 18 | 12 | 4 |  | 1 | 2 | TempC 15 |  |  | int16 | Read | Temperature of 1-wire-sensor 15
| 30020 | 19 | 13 | 4 |  | 1 | 2 | TempC 16 |  |  | int16 | Read | Temperature of 1-wire-sensor 16
STATUS DATA * Read this data to know the RF signal strength of sensor node and reliability of received data | 40029 | 28 | 1C | 3 |  | 1 | 2 | Data status of Node | 0-9, 99 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40069 | 68 | 44 | 3 |  | 1 | 2 | RF Signal strength of Node | 0-4 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only
| 40189 | 188 | BC | 3 |  | 1 | 2 | Sync status of Node | 0-2 |  | byte | Read | If the Node ID is odd ==> read the Hi-Byte only If the Node ID is even ==> read the Lo-Byte only | for sensor with V5.x
ADVANCED CONFIG * Use this only in case of changing the default values of configuration parameters | 40401 | 400 | 190 | 3 | 16 | 1 | 2 | Cycle_wakeup | 1-3600(s) | 120 | uint16 | Read/Write | Every time interval of Cycle_wakeup, sensor node would ONLY send data to co-ordinator if the new measured value was changed more than the Delta value of the last measured value. Default Cycle_wakeup is 120 seconds | for sensor with V5.x
| 40402 | 401 | 191 | 3 | 16 | 1 | 2 | Cycle_healthsta | 60-7200(s) | 600 | uint16 | Read/Write | Every time interval of Cycle_healthsta, sensor node will absolutely send data to co-ordinator regardless any condition | for sensor with V5.x
| 40403 | 402 | 192 | 3 | 16 | 2 | 4 | Co-ordinator id |  | 0 | uint32 | Read/Write | Configure the ID number of Co-ordinator that wireless sensor want to connect to the Co-ordinator when only adding the sensor manually | for sensor with V5.x
| 40405 | 404 | 194 | 3 | 16 | 2 | 4 | Radio frequency | 433.05-434.79, 433 Mhz | 433.92 | float | Read/Write | Configure the operating frequency of wireless sensor by Co-ordinator, should be configured from 433.05-434.79 MHz, only for advanced users | for sensor with V5.x
| 40407 | 406 | 196 | 3 | 16 | 1 | 2 | Tx power | -10,10,15 | 15 | int16 | Read/Write | Configure the RF power of wireless sensor by Co-ordinator, only for advanced users + 15 <=> tx power = 15dBm + 10 <=> tx power = 10dBm + -10 <=> tx power = -10dBm | for sensor with V5.x
| 40408 | 407 | 197 | 3 | 16 | 1 | 2 | Data rate RF | 0-1 | 0 | uint16 | Read/Write | Configure the air data rate of wireless sensor by Co-ordinator, only for advanced users + 0 <=> data rate RF at 50kbps + 1 <=> data rate RF at 625bps | for sensor with V5.x
| 40409 | 408 | 198 | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40411 | 410 | 19A | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40413 | 412 | 19C | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40415 | 414 | 19E | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40417 | 416 | 1A0 | 3 | 16 | (5): 2; (6): 4; (7): spare; * A standard register in Modbus is a WORD (2 bytes, comprise Hi-Byte and Lo-Byte) (13): for sensor with V5.x
| 40419 | 418 | 1A2 | 3 | 16 | 1 | 2 | 1wire id 1 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40420 | 419 | 1A3 | 3 | 16 | 1 | 2 | 1wire id 2 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40421 | 420 | 1A4 | 3 | 16 | 1 | 2 | 1wire id 3 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40422 | 421 | 1A5 | 3 | 16 | 1 | 2 | 1wire id 4 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40423 | 422 | 1A6 | 3 | 16 | 1 | 2 | 1wire id 5 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40424 | 423 | 1A7 | 3 | 16 | 1 | 2 | 1wire id 6 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40425 | 424 | 1A8 | 3 | 16 | 1 | 2 | 1wire id 7 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40426 | 425 | 1A9 | 3 | 16 | 1 | 2 | 1wire id 8 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40427 | 426 | 1AA | 3 | 16 | 1 | 2 | 1wire id 9 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40428 | 427 | 1AB | 3 | 16 | 1 | 2 | 1wire id 10 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40429 | 428 | 1AC | 3 | 16 | 1 | 2 | 1wire id 11 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40430 | 429 | 1AD | 3 | 16 | 1 | 2 | 1wire id 12 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40431 | 430 | 1AE | 3 | 16 | 1 | 2 | 1wire id 13 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40432 | 431 | 1AF | 3 | 16 | 1 | 2 | 1wire id 14 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40433 | 432 | 1B0 | 3 | 16 | 1 | 2 | 1wire id 15 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40434 | 433 | 1B1 | 3 | 16 | 1 | 2 | 1wire id 16 |  |  | hex | Read/Write | Read to check 1-wire-sensor id. Write 0 to delete this sensor
| 40435 | 434 | 1B2 | 3 | 16 | 1 | 2 | run mode |  |  | unit16 | Read/Write | 0: add 1wire, 1: read tempC
| 40436 | 435 | 1B3 | 3 | 16 | 1 | 2 | read retry times |  | 0 | unit16 | Read/Write
| 40001 | 0 | 0 | 16 |  | 11 | 22 | Spare |  |  |  | Read/Write | Not Applicable | for sensor with V5.x
| 40012 | 11 | B | 16 |  | 1 | 2 | Enb_update_data_frame & Data_numblock |  | 00 01 | hex | Read/Write | Data frame definition, only for advanced users. Write "Enb_update_data_frame" = 0x19 => allow sensor Node to write the setting values of Data_numblock, Data_reg & Data_numreg in its Flash | for sensor with V5.x
| 40013 | 12 | C | 16 |  | 1 | 2 | Data_reg1 & Data_numreg1 |  | 08 17 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x
| 40014 | 13 | D | 16 |  | 1 | 2 | Data_reg2 & Data_numreg2 |  | 00 00 | hex | Read/Write | Data frame definition, only for advanced users | for sensor with V5.x